## Slide 1
Fire Inspection and Code Enforcement
8th Edition Inspector I
Chapter 13 — Special-Agent Fire Extinguishing Systems and Portable Extinguishers

## Slide 2: Learning Objective 1
Describe the components and operation of fixed fire suppression systems.

## Slide 3: Know why special-agent fire extinguishing systems are used.
Fixed or mobile suppression systems are used in locations where standard automatic sprinkler systems are not the most effective way to address a particular fire risk

## Slide 4: Know where special-agent fire extinguishing systems are used.
Flammable and combustible liquids
Water-reactive metals or chemicals
Combustible metals that are flammable solids
Food preparation equipment
File storage or archives
Electronic Information Technology (IT) equipment
Electrical transformers and switches
High-value content such as museums
Courtesy of Rich Mahaney

## Slide 5: Special-agent fire extinguishing systems operate with a specific, limited, quantity of agent.
Must completely extinguish the fire to be considered successful
A variety of systems exist

## Slide 6: Understand how special-agent fire extinguishing systems are classified.
By the type of fire they will extinguish
Labels may be affixed to the extinguishing agent storage tanks to indicate the class of fire for which the system is approved
(Cont.)

## Slide 7: NOTE
Portable fire extinguishers are also classified and labeled according to the type of fire they will extinguish.

## Slide 8: Understand how special-agent fire extinguishing systems are classified.
Class A
Involves ordinary, solid, combustible materials such as wood, cloth, paper, rubber, and many plastics
Class B
Involves flammable and combustible liquids and gases such as gasoline, oil, lacquer, paint, mineral spirits, and alcohol
(Cont.)

## Slide 9: Understand how special-agent fire extinguishing systems are classified.
(Cont.)
Class C
Involves energized electrical equipment where the electrical nonconductivity of the extinguishing agent is of major importance
Class D
Involves combustible metals such as aluminum, magnesium, potassium, sodium, titanium, and zirconium (particularly in their powdered forms)
Materials involved are either Class A (wiring insulation) or Class B (lubricants)
Can be extinguished once the equipment is de-energized
May require special extinguishing agents or techniques

## Slide 10: Understand how special-agent fire extinguishing systems are classified.
Class K
Involves oils and greases normally found in commercial cooking kitchens and food preparation facilities using deep fryers
Through a process known as saponification, extinguishing agents turn fats and oils into a soapy foam that extinguishes a fire

## Slide 11: NOTE
Class K is the most recently added classification of fire designated by NFPA®. It reflects the development and use of cooking oils that have extremely high combustion temperatures that require special extinguishing agents. In Europe this classification is designated as Class E.

## Slide 12: REVIEW QUESTION
Define the different fire classifications.

## Slide 13: Know when dry-chemical extinguishing systems are used.
Used wherever rapid fire extinguishment is required and where reignition of the burning material is unlikely

## Slide 14: Know what dry-chemical extinguishing systems are commonly used to protect.
Flammable liquid storage rooms
Dip tanks
Paint spray booths
Exhaust duct systems

## Slide 15: Understand inspection duties for dry-chemical extinguishing systems.
Review installation plans
Review manufacturers’ specification sheets (cut sheets)
Inspect new installations
Witness acceptance tests of new installations
Perform periodic inspections of existing systems

## Slide 16: Know the application methods for dry-chemical extinguishing systems.
Fixed system
Handheld hoseline

## Slide 17: Know the characteristics of fixed extinguishing systems.
Components
Consists of agent storage tanks, expellant storage tanks, heat-detection and activation system, piping, and nozzles
Local application: most common type; discharges agent onto a specific surface such as the cooking area in a restaurant kitchen
Total flooding: introduces a concentration of agent into a closed area such as a spray paint booth
Two main types

## Slide 18: Know the characteristics of handheld hoseline extinguishing systems.
Requires trained personnel to apply dry chemical from hose stations connected directly to the agent and expellant storage containers
Hose stations contain hoseline and nozzle assemblies that can reach all portions of the protected area
Some types of hazards may require installation of handheld hoselines

## Slide 19: REVIEW QUESTION
Name types of dry-chemical application methods.

## Slide 20: Know the characteristics of dry-chemical agents.
Used in situations where water would be ineffective or reactive with the burning materials
Extinguish fire by separating the oxygen from the fuel; inhibiting the chemical chain reaction necessary for combustion
Generally the same agents that are used in portable fire extinguishers

## Slide 21: Understand the disadvantages of dry-chemical agents.
Not recommended for an area that contains sensitive electronic equipment
Some may become corrosive when exposed to moisture
Discharge a cloud of chemicals that leave a residue, creating a cleanup problem
Chemical residue has insulating characteristics that hinder the operation of the equipment unless extensive cleanup is performed

## Slide 22: Know the different kinds of dry-chemical agents.
Sodium bicarbonate
Twice as effective for Class B fires than an equal weight of carbon dioxide (CO2)
Very rapid control capability against flaming combustion
Used successfully on textile machinery where the concentration of fine textile fibers can produce a surface fire
Used in fire extinguishing systems that are chemically treated to be water-repellent and free-flowing
Also known as ordinary dry chemical
Effective on Class B and Class C fires
Has some effect on surface fires in Class A materials
(Cont.)

## Slide 23: Know the different kinds of dry-chemical agents.
Potassium bicarbonate
Most effective on Class B and Class C fires
On a pound-for-pound basis, potassium bicarbonate can extinguish a fire twice the size that the same amount of sodium bicarbonate can
Potassium bicarbonate is also treated to be water-repellent and free-flowing
Also known as Purple-K
Properties and applications similar to sodium bicarbonate
(Cont.)

## Slide 24: Know the different kinds of dry-chemical agents.
Monoammonium phosphate
Acts similar to other dry chemicals on flammable liquid fires
Using a combination of extinguishing methods, it quickly extinguishes flaming combustion
On ordinary combustible materials, it melts, forming a solid coating that extinguishes the fire by smothering
Because it can have a corrosive effect on unprotected metals, corrosion can form around extinguisher system nozzles, piping, and agent containers
Also known as multipurpose dry-chemical (pale yellow in color)
Effective on Class A, Class B, and Class C fires

## Slide 25: Know the components included in a dry-chemical system.
Storage container for agent and/or expellant gas
May contain both the agent and pressurized expellant gas (either nitrogen or carbon dioxide), or they may be stored in separate containers
(Cont.)

## Slide 26: Know the components included in a dry-chemical system.
Storage container for agent and/or expellant gas
Pressure gauge attached to the storage container indicates the stored pressure of the container
Typical range from 30 to 100 pounds (15 kg to 50 kg)
Must also be in an area that maintains a temperature range from -40°F to 120°F (-40°C to 50°C)
Must be located as close to the discharge point as possible
(Cont.)

## Slide 27: Know the components included in a dry-chemical system.
Piping to carry the agent and gas
Engineered to account for the unique flow of the agent
Pipe configuration must be calculated into the design
No standard nozzle designs exist
Each system manufacturer has its own designs and nozzles
Attached to a system of fixed piping to deliver the agent to the hazard
Nozzles
Must be listed in accordance with NFPA® 17
(Cont.)

## Slide 28: Know the components included in a dry-chemical system.
Actuating mechanism
In many cases it occurs after the melting of fusible links but may be activated by smoke, optical, or other forms of fire detection
Releases agent into the piping system in response to the activation of a fire detection system
Detection device triggers a mechanical or electrical release that in turn triggers the flow of agent and expellant gas
(Cont.)

## Slide 29: Know the components included in a dry-chemical system.
Actuating mechanism
Automatic actuation should also have audible signals
Exiting the area quickly lessens reduced visibility or breathing issues
Majority of fixed systems must also be capable of manual release and equipped with automatic fuel or power shutoffs

## Slide 30: Know who is responsible for the components of dry-chemical systems.
Fire protection companies
Owner/occupant representatives/fire inspectors
Detailed maintenance of these systems
Be aware of changes in hazards and be able to evaluate these systems for several conditions
Courtesy of George Apple

## Slide 31: REVIEW QUESTION
List the components in a dry-chemical extinguishing system.

## Slide 32: Dry powders are designed to extinguish Class D fires.
Includes fires involving aluminum, magnesium, sodium, and potassium
No single agent is effective on all combustible metals
Metal fires produce extreme heat and require a long period for complete extinguishment
Extinguishing agent must be carefully chosen for the hazard metal being protected

## Slide 33: Be familiar with the most common Class D agents.
NA-X®
Forms an encasing crust or cake on the burning material
Listed by Underwriters Laboratories Inc. (UL) for use on burning materials at fuel temperatures up to 1,400°F (760°C)
Sodium carbonate-based agent with additives to enhance its flow
Designed specifically for use on sodium, potassium, and sodium-potassium alloy fires
NOT suitable for use on magnesium fires
Application can be from fixed systems, by hand from pails, or from portable extinguishers
(Cont.)

## Slide 34: Be familiar with the most common Class D agents.
MET-L-X®
Extinguishes metal fires by forming a crust
Nonabrasive and has no known toxic effects
Sodium chloride (salt) based agent intended for use on magnesium, sodium, and potassium fires
Contains additives to enhance flowing and prevent caking in the extinguisher
Applied from the extinguisher to first control the fire and then it is applied more slowly
Stable when stored in sealed containers
(Cont.)

## Slide 35: Be familiar with the most common Class D agents.
LITH-X®
Developed to control fires involving lithium
Does not form a crust on the burning metal
Graphite based agent that extinguishes fires by conducting heat away from the fuel after a layer of the powder has been applied
Can be used on several combustible metals
Can be used to extinguish magnesium, zirconium, and sodium fires

## Slide 36: REVIEW QUESTION
Identify the common agents used in dry powder systems.

## Slide 37: Understand the characteristics of wet-chemical systems.
Most effective on fires in commercial cooking equipment
Extinguishes oil fires by fuel removal, cooling, smothering, and flame inhibition
Agents react with animal or vegetable oils and form a soapy foam

## Slide 38: Understand the differences in wet- and dry-chemical systems.
Primary difference is the type of agent used
May find some dry-chemical systems protecting some cooking equipment even though tests and fire analyses have indicated they do not meet the criteria for extinguishing fires involving deep-fat fryers

## Slide 39: Be familiar with wet-chemical agents.
Typically composed of water and either potassium carbonate, potassium citrate, or potassium acetate
Delivered to the hazard area in the form of a spray

## Slide 40: REVIEW QUESTION
Differentiate between dry-chemical systems and wet-chemical systems.

## Slide 41: Clean-agent systems include extinguishing agents that leave no residue.
Effective on Class A, Class B, and Class C fires
Approved by the EPA as nonharmful to the atmosphere
Will not conduct electricity
NFPA® 2001, Standard on Clean Agent Fire Extinguishing systems, describes the requirements for total flooding and local application clean-agent extinguishing systems

## Slide 42: Understand how clean agents are stored and deployed.
Stored as liquefied compressed gas
Extinguishes fire by displacing oxygen and disrupting the fire tetrahedron
Not appropriate for occupied areas
Release agents that are potentially unhealthy or that will cause asphyxiation
Convert to a gas when exposed to air

## Slide 43: Know where clean-agent systems are commonly used.
Computer rooms
Telecommunications facilities
Clean (manufacturing) rooms
Document archives and art storage rooms
Laboratories
Where contents are delicate, sensitive to water or other corrosives

## Slide 44: Understand why inspectors need to be familiar with halon systems.
Were the first groups of clean agents developed
Principally effective on Class B and Class C fires
The term halon has been commonly used to describe this group of agents
Halon production has been discontinued, but systems can remain in service until they need to be replaced or upgraded

## Slide 45: Inspectors should know the two types of halons still in use.
Halon 1211 (bromochlorodifluoromethane)
Used in some portable fire extinguishers but is more commonly found in fixed total flooding systems
Halon 1301 (bromotrifluoromethane)
Most commonly found in portable fire extinguishers

## Slide 46: NOTE
Halon materials may be recycled. Recycling reduces the material’s volume by approximately ten percent each time it is recycled. The sale and storage of halon materials from the existing stockpiles is still permitted, so an inspector may find a facility with large amounts stored.

## Slide 47: Be familiar with the clean agents now commercially available.
Halotron®
Leaves no residue
Does not conduct electricity, making it suitable for Class C fires
Halocarbon agent that becomes a rapidly evaporating liquid when discharged
FM-200™
Halocarbon agent that leaves no residue
Meets EPA minimum standards for discharge into the atmosphere
Not harmful to humans or the environment
Requires significantly more agent to achieve extinguishment
(Cont.)

## Slide 48: Be familiar with the clean agents now commercially available.
Inergen®
ECARO-25™
Can be used in an existing halon system with only the replacement of the storage container and discharge nozzles
Third-party testing indicates that it is safe for human exposure in very short durations
Blend of three naturally occurring gases
Environmentally safe
Does not contain a chemical composition
Stored in cylinders near the facility under protection
Hydrofluorocarbon-based agent that is nonconductive, noncorrosive, residue free
Zero ozone-depletion potential (ODP)
Environmentally preferred to halon
(Cont.)

## Slide 49: Be familiar with the clean agents now commercially available.
FE-36™
Consists of hydrofluorocarbon HFC-236fa
Suggested applications include computer and telecommunications rooms, museums and archives, hospitals, auto racetracks, and on aircraft
Developed by DuPont™ to replace both Halon 1301 in local application systems and Halon 1211 in portable fire extinguishers

## Slide 50: Understand the components included in a clean-agent system.
May be fixed systems that are designed for local application or total flooding agent distribution
System components include actuation devices, agent storage containers, piping, and discharge nozzles

## Slide 51: REVIEW QUESTION
What components are included in a clean-agent fire extinguishing system?

## Slide 52: Understand the characteristics of a carbon dioxide system.
Clean agent proven effective at extinguishing fires involving many types of combustible materials
Less effective at extinguishing fires involving nitrates that contain available oxygen, and not suitable for fires involving metals
Limitations of CO2 are related to health effects associated with its use as well as restrictions imposed by the combustible material itself
Resemble clean-agent extinguishing systems
All systems must adhere to requirements as described in NFPA® 12, Standard on Carbon Dioxide Extinguishing Systems

## Slide 53: Know what material or equipment fires CO2 has extinguished.
Flammable and combustible liquids
Electrical equipment and energized equipment, including power plants and large standby generators
Flammable gases
Other combustibles including cellulose materials

## Slide 54: Understand the cooling effects of CO2 systems.
As delivered, CO2 is extremely cold, approaching -110°F (-80°C)
Limited cooling effect on a fire
Primary mechanism is oxygen removal or smothering in the box
Limited cooling effects occur when applied directly to the burning material
Can freeze exposed skin

## Slide 55: Know what types of hazardous facilities utilize CO2 systems.
Automobile manufacturing facilities
Industrial plants
Refineries/ chemical plants
Paint and coating operations
Food/agricultural processing plants
Pharmaceutical manufacturing facilities
Power plant and large standby generators
Large printing presses

## Slide 56: NOTE
Handheld hoseline and standpipe systems are also used although they are not common and not addressed in this manual.

## Slide 57: The most serious problem involving CO2 systems is personnel safety.
Carbon dioxide
Asphyxiant
Eliminates oxygen from a fire
Eliminates breathable oxygen from the atmosphere
Total flooding systems are of specific concern
(Cont.)

## Slide 58: The most serious problem involving CO2 systems is personnel safety.
Total flooding system
Designed to deliver at least 34 percent concentration of CO2 into an enclosed area; Concentrations this high are lethal to humans
All affected personnel must be educated about the dangers; trained in proper emergency procedures related to system discharge
Systems must be provided with predischarge and discharge alarms
Room integrity
Critical for total flooding to be effective
Inspectors must be able to evaluate the integrity of a room
NFPA® 2001 requires annual room integrity tests; inspectors should make a visual inspection of rooms; look for obvious issues or changes
Includes several components

## Slide 59: Local application systems are not as dangerous as total flooding systems.
CO2 is delivered directly onto the fire as opposed to filling an enclosure
Danger to personnel is reduced if the local application system is located outdoors or in a large building

## Slide 60: REVIEW QUESTION
Why are CO2 systems dangerous to personnel?

## Slide 61: Understand the components of CO2 systems.
Similar to those of clean-agent fire extinguishing systems
Actuation devices
Agent storage containers
Piping
Discharge nozzles

## Slide 62: Be familiar with the actuation for CO2 systems.
Automatic operation
Normal manual operation (pictured)
Initiated by a listed form of smoke or fire detection device
Trigger control valves on the CO2 supply that allow the agent to enter the system and discharge
Initiated by a person manually operating a control device and putting the system through its complete cycle of operation, including predischarge alarms
(Cont.)

## Slide 63: Be familiar with the actuation for CO2 systems.
Emergency manual operation
Used only when the other two actuation modes fail
Causes the system to discharge immediately and without any warning to individuals in the area

## Slide 64: CO2 systems exist as either high-pressure or low-pressure systems.
High-pressure systems
CO2 stored in standard DOT-approved cylinders at a pressure of about 850 psi (5 950 kPa)
(Cont.)

## Slide 65: CO2 systems exist as either high-pressure or low-pressure systems.
Low-pressure
Designed to protect much larger hazards
Liquefied CO2 is stored in large, refrigerated tanks at 300 psi (2 100 kPa)
Courtesy of Chemetron Fire Systems
(Cont.)

## Slide 66: CO2 systems exist as either high-pressure or low-pressure systems.
In either a high- or low-pressure system, containers are connected to discharge nozzles through a system of fixed piping
Nozzles for total flooding systems may be high- or low-velocity types
Local application nozzles are typically the low-velocity type; reduces the possibility of splashing the burning product when the agent contacts it
High-velocity nozzles promote better agent disbursement throughout the entire area

## Slide 67: REVIEW QUESTION
List the means of actuation for CO2 systems.

## Slide 68: Foam extinguishing systems are used in locations where water alone may not be effective.
Flammable liquids processing or storage facilities
Aircraft hangars
Rolled paper- or fabric-storage facilities

## Slide 69: Know the different ways foam extinguishes fire.
Smothering – Prevents air and flammable vapors from combining
Separating – Intervenes between the fuel and the fire
Cooling – Lowers the temperature of the fuel and adjacent surfaces
Suppressing – Prevents the release of flammable vapors

## Slide 70: Inspectors need to know how foam fire extinguishing systems work.
When applied at the correct rate of discharge, foam suppresses fire by forming a chemical layer that is resistant to air on the liquid surface and absorbs heat
The water in the foam solution absorbs additional heat, which suppresses further production of vapors and protects against re-ignition
The type of system and foam used depend on the hazard being protected

## Slide 71: Foam fire extinguishing systems require several items to operate.
Adequate water supply
Foam concentrate supply
Piping system
Proportioning equipment
Foam discharge devices

## Slide 72: Know the different types of foam fire extinguishing systems.
Fixed
Automatically discharges foam through fixed delivery outlets to the protected hazard
If a pump is required to increase pressure on the system, it is usually permanently installed
Complete installation piped from a central foam station
(Cont.)

## Slide 73: Know the different types of foam fire extinguishing systems.
Semifixed
Primarily used on flammable liquid storage tanks
Found in settings that involve several similar hazards such as petroleum refineries
Foam discharge piping is in place but not attached to a permanent source of foam; requires a separate mobile foam-solution source, usually a fire brigade or fire department pumper/truck
(Cont.)

## Slide 74: Know the different types of foam fire extinguishing systems.
Mobile
Portable
Wheel-mounted, foam fire extinguishing system
Hand-transported foam-producing equipment, such as hose, nozzle, proportioner, and other materials
May contain premixed foam solution or have water supply connection capability
Can be self-propelled or towed by a vehicle

## Slide 75: Understand the items involved in foam fire extinguishing systems.
Foam concentrate
Foam proportioner
Foam solution
Foam
Raw foam liquid before the introduction of water and air
Usually shipped in 5-gallon (20 L) buckets or 55-gallon (220 L) drums
Stored in large fixed tanks that can hold 500 gallons (2 000 L) or more
Device that introduces the correct amount of concentrate into the water stream to make the foam solution
Homogeneous mixture of foam concentrate and water before the introduction of air
Completed product once air is introduced into the foam solution

## Slide 76: Four elements are necessary to produce high-quality fire fighting foam.
All of elements must be present and blended in the correct proportions
Removing any element will result in either no foam or poor-quality foams

## Slide 77: There are two stages in the formation of foam.
Proportioning
Water mixed with foam liquid concentrate to form foam solution
Foam solution passes through the system piping
Travels to the foam distribution nozzle or sprinkler
(Cont.)

## Slide 78: There are two stages in the formation of foam.
Foam solution reaches distribution nozzle or sprinkler
Air added (aeration)
Foam solution changed into finished foam
Aeration

## Slide 79: Inspectors may need to become familiar with a variety of types of foam production equipment.
Proportioning equipment and foam nozzles or sprinklers are engineered to work together
Inspector will inspect or analyze different types of foam fire extinguishing systems
Using a foam proportioner that is not hydraulically engineered and matched with the foam distributor nozzle or sprinkler can result in unsatisfactory quality foam or no finished foam at all

## Slide 80: Understand the general foam proportioning rates.
Finished foam is 94 to 99½ percent water
Class B low-expansion foams in use today are designed to be used at 1-percent, 3-percent, or 6-percent concentrations
Foam designed for hydrocarbon fires are used at 1-percent to 6-percent concentrations
Polar solvent fuels require 3-percent or 6-percent concentrates
Medium- and high-expansion foams are typically used at 1-percent, 1½-percent, 2-percent, or 3-percent concentrations

## Slide 81: Foam concentrate is designed for low, medium, and high expansion rates, depending on its purpose.
Low
Low-expansion foam is most effective when the temperature of the liquid fuel does not exceed 212°F (100°C)
If the fuel temperature exceeds this figure, much higher foam expansion rates will be required in order to cool the fuel
Small air/solution ratio
Used primarily to extinguish fires involving liquid fuels
Also used for vapor suppression on unignited liquid fuel spills
(Cont.)

## Slide 82: Foam concentrate is designed for low, medium, and high expansion rates, depending on its purpose.
Medium
Can be used indoors or outdoors on either solid or liquid fuels
Will produce more foam with less water than the low-expansion type foams
Typically has expansion ratios between 20:1 and 200:1; used when rapid vapor suppression is needed
(Cont.)

## Slide 83: Foam concentrate is designed for low, medium, and high expansion rates, depending on its purpose.
High
Generally has expansion ratios of 200:1 to about 1,000:1
Useful as a space-filling agent in aircraft hangars, hard-to-reach spaces, and bulk-baled commodities
Steam dilution caused by vaporization of the foam in heated areas displaces gas and smoke, thus cooling the environment and extinguishing confined-space fires
Courtesy of the United States Air Force

## Slide 84: Inspectors need to research before inspecting foam extinguishing systems.
UL and NFPA® 11, Standard for Low-, Medium-, and High-Expansion Foam, to determine recommended uses
Manufacturer’s information sheets to determine proper storage of foam, its shelf life, and how to dispose of it without damaging the environment

## Slide 85: Know the characteristics of foam concentrates.
Foam concentrates must match the fuel to which they are applied
Foams designed for hydrocarbon fires will not extinguish polar solvent fires, regardless of the concentration at which they are used
Foam concentrate is manufactured with either a synthetic or protein base
Some foam concentrates are a combination of the two
Foams that are designed for polar solvent fires may be used on hydrocarbon fires

## Slide 86: There are several types of concentrates an inspector may encounter.
Fluoroprotein foam
Film forming fluoroprotein (FFFP) foam
Aqueous film forming foam (AFFF)
Alcohol-resistant aqueous film forming foam (AR-AFFF)

## Slide 87: Know the characteristics of balanced pressure proportioners.
Balanced pressure proportioner
Foam concentrate pump supplies the concentrate line from a fixed storage tank
Foam concentrate and water supplied at the same pressure
One of the most reliable methods of foam proportioning
Concentrate lines connected to each fire pump discharge outlet or to the system riser
(Cont.)

## Slide 88: Know the characteristics of balanced pressure proportioners.
Advantages
Ability to monitor the demand for foam concentrate; adjust the amount
Ability to discharge foam concentrate from some outlets and plain water from others at the same time
Discharge orifice is adjustable at the point where it connects to the system riser

## Slide 89: Know the characteristics of around-the-pump proportioners.
Around-the-pump proportioner
Rated for a specific flow
Has a small return line from the discharge side of a fire pump back to the intake side of the pump
Inline eductor is positioned on the bypass line
Useful when there is low water pressure or when a motor is not available
Most common type of built-in proportioner installed in mobile fire apparatus and some fixed system applications
(Cont.)

## Slide 90: Know the characteristics of around-the-pump proportioners.
Disadvantages
Does not allow plain water and foam concentrate to be discharged from the pump at the same time
Pumps cannot take advantage of incoming pressure
Pump must be dedicated solely to foam operation

## Slide 91: Know the characteristics of pressure proportioning tank systems.
Pressure proportioning tank system
Water volumetrically displaces the concentrate, forcing it into the foam solution line where it is mixed with discharge water
Allows for automatic proportioning over a wide range of flows and pressures
System is limited by the size of the concentrate tank
Consists of one or two foam concentrate tanks that connect to both the water supply and foam solution lines of the overall system
Designed so a small amount of water from the supply source is pumped into the concentrate tank(s)
Does not depend on an external power source

## Slide 92: Know the characteristics of coupled water motor-pump proportioners.
Coupled water motor-pump proportioner
As water flows through the larger pump, it causes the smaller pump to turn; draft foam concentrate from the foam tank
Correct foam/water solution results because the pumps are sized in proportion to each other
Used in fixed-system applications
Consists of two positive-displacement rotary-gear pumps mounted on a common shaft
Larger pump is for water and the smaller one is for the foam concentrate
Limited to two sizes, both designed for 6-percent proportioning rates

## Slide 93: REVIEW QUESTION
Explain how foam proportioners operate.

## Slide 94: Learning Objective 2
Explain how to determine the operational readiness of portable fire extinguishers.

## Slide 95: A portable fire extinguisher can provide the first line of defense against an incipient fire.
The value of a fire extinguisher lies in the speed with which it can be used
Person using the extinguisher must understand how it operates and be physically capable of operating it

## Slide 96: To be effective, a fire extinguisher requires several items.
Readily visible and accessible
Suitable for the hazard being protected
Properly maintained
Of sufficient size to control an incipient fire
Used in appropriate wind and weather conditions to provide effective application on exterior fires

## Slide 97: Know where to find requirements for portable fire extinguishers.
NFPA® 10, Standard for Portable Fire Extinguishers
Locally adopted codes

## Slide 98: Understand the classification system for portable fire extinguishers.
No single portable fire extinguisher is suitable for use on every type of burning fuel
Fire extinguishers are classified by the type of fire they will extinguish
Labels are affixed to the extinguishers to indicate the class of fire for which the extinguisher is approved
Five classifications of fires include A, B, C, D, and K

## Slide 99: Portable fire extinguishers are rated according to their intended use and extinguishing capabilities.
Type and amount of extinguishing agent and extinguisher’s design determine the amount of fire that can be extinguished for a particular class of fire
Information is displayed on the front faceplate of the extinguisher; uses an alphanumeric classification system
Multiple letters or numerical-letter ratings are used for portable fire extinguishers that are effective on more than one class of fire
Class A and Class B extinguishers also receive a numerical rating that precedes the letter; designates the size of fire the extinguisher can be expected to extinguish when used by an untrained operator
(Cont.)

## Slide 100: Portable fire extinguishers are rated according to their intended use and extinguishing capabilities.
(Cont.)

## Slide 101: Portable fire extinguishers are rated according to their intended use and extinguishing capabilities.
Occupants who need to use a fire extinguisher are usually under stress and in a hurry, so a labeling system that includes both an icon and the alphanumeric rating is desirable
Fire extinguisher rating labels are designed to enable a user to identify the type of fire extinguisher without having to understand the A-B-C-D-K rating system
To simplify the process of matching extinguishers with types of fires, several methods for identifying extinguishers by using symbols or icons have been developed

## Slide 102: NFPA® 10 recognizes two methods of extinguisher recognition: the pictorial or the letter-symbol system.

## Slide 103: REVIEW QUESTION
Describe the pictorial symbols used for the different classes of fire.

## Slide 104: Understand the characteristics of agents used in portable fire extinguishers.
Portable fire extinguishers use many different types of extinguishing agents
Each extinguishing agent may be able to control one or more classes of fire
Agents are the same as those used in the dry-chemical fixed fire extinguishing and handheld hoseline systems
One agent cannot extinguish all classes of fire

## Slide 105: Understand water-type fire extinguishers.
Characteristics
Most common size of water extinguisher is the 2½-gallon (10 L) model
Relatively easy to maintain but subject to freezing
Limited by amount of water carried in a portable unit
Limitations
Ineffective by itself on most Class B fires
Conducts electricity; dangerous on Class C electrical fires
Reactive with some chemicals and Class D metals
Can cause heated cooking oils to splatter
Maximum size that is considered portable is the 5-gallon (20 L) unit
Must be kept in a heated area unless an approved antifreeze agent is added to the water
Liquid used to extinguish fires in Class A materials primarily by cooling the burning fuel

## Slide 106: Understand carbon dioxide (CO2) fire extinguishers.
Characteristics
Extinguishes primarily through a smothering action
Colorless, noncombustible gas that is heavier than air
Suitable for Class B and Class C fires
Store CO2 in a liquid state
Has a white cloudy appearance when discharged
(Cont.)

## Slide 107: Understand carbon dioxide (CO2) fire extinguishers.
Limitations
Limited value on Class A fires that are located deep within the burning material
Difficult to project CO2 very far from the extinguisher
Its temperature has a minimal effect in cooling or extinguishing a fire
Discharges with a loud noise
May be a discharge of static electricity that can shock the operator when operated in areas of low humidity

## Slide 108: WARNING
Carbon dioxide (CO2) is an asphyxiant. Do not use a CO2 extinguisher in a confined space without supplied-air respiratory protection.

## Slide 109: Understand foam agent fire extinguishers.
Characteristics
Suitable for Class A and Class B fires
Most commonly, foam concentrate is premixed in the extinguisher and discharged through a special aerating nozzle
Concentrate added to water to increase effectiveness; may contain aqueous film forming foam (AFFF) or film forming fluoroprotein (FFFP) foam solutions
(Cont.)

## Slide 110: Understand foam agent fire extinguishers.
Effectiveness features
Effective on Class A fuels
Penetrates deeply into tightly packed fuels
Very effective on flammable liquid fires

## Slide 111: Understand dry chemical fire extinguishers.
Characteristics
Frequently used agents
Potassium bicarbonate
Monoammonium phosphate (multipurpose)
Urea potassium bicarbonate
Potassium chloride
Do not dissipate into the atmosphere as rapidly as gases
Especially suitable for controlling fires outdoors
Sodium bicarbonate

## Slide 112: Understand wet chemical fire extinguishers.
Characteristics
Agent is delivered to the hazard area in the form of a spray
Intended for use with Class K fixed systems or commercial kitchens that have deep fat fryers using vegetable or animal fats
Inspectors should determine the type of agent in use; verify that the portable extinguishers mounted in the kitchen are compatible
Solution composed of water and potassium carbonate, potassium citrate, or potassium acetate

## Slide 113: Understand clean agent fire extinguishers.
Characteristics
Two halons are still in use in portable fire extinguishers
Halon 1211 is most commonly found in portable fire extinguishers
Halon 1301 is used in some portable fire extinguishers; more common in fixed-system applications
Extinguishers using halon replacements contain inert gases such as argon or DuPont FE-36™
Extinguishers available in a variety of capacities and may cover 5 to 25 square feet (0.45 m2 to 2.25 m2)
Leaves no residue when discharged

## Slide 114: CAUTION
It is very important to use the correct extinguishing agent on a fire. Using the wrong agent can be dangerous and can result in a fire not being extinguished, a violent reaction, or both.

## Slide 115: Know the characteristics of stored-pressure extinguishers.
Contains expellant gas and extinguishing agent in a single chamber
Pressure of the gas forces the agent out through a siphon tube into the chamber, valve, and nozzle assembly
Usually requires special charging equipment for pressurization
Licensed distributors usually perform needed services
Normally found in locations where a high-use factor is not expected
Air-pressurized water (APW) extinguishers are the most common

## Slide 116: Know the characteristics of cartridge-operated extinguishers.
Stores expellant gas in a separate cartridge attached to the side of the agent cylinder or tank
During activation, expellant gas is released into the agent cylinder
Discharge is controlled by a handheld nozzle/lever; no pressure gauge is provided
Found in industrial operations
When recharging, replace the gas cartridge and fill the agent cylinder
Pressure of the gas forces the agent into the application hose
Inspectors should verify that the expellant gas cartridge has not been activated; weigh to be sure that it has adequate gas

## Slide 117: Know the characteristics of pump-operated extinguishers.
Discharges agent by the manual operation of a pump
Only water can be used in this type of extinguisher
Not generally found outside fire departments or fire brigades
Maintenance is extremely simple
Primary advantage is that it can be refilled from any available water source

## Slide 118: Know how to spot a properly placed fire extinguisher.
Visible and marked with legible signage
Not blocked by storage or equipment
Near points of egress or ingress
Near normal paths of travel
Placed in proper physical environment for extinguisher

## Slide 119: Properly securing extinguishers to the structure will prevent injury and damage.
Extinguishers are frequently placed in cabinets or wall recesses to protect both the extinguisher and people who might walk into them
If an extinguisher cabinet is placed in a fire-rated wall, the cabinet must have the same fire-resistance rating as the wall assembly

## Slide 120: Extinguishers need to be placed so that they are easy to access.
Extinguishers with a gross weight not exceeding 40 pounds (18 kg) should be installed so that the top of the extinguisher is not more than 5 feet (1.5 m) above the floor
Extinguishers with a gross weight greater than 40 pounds (18 kg), except wheeled types, should be installed so that the top of the extinguisher is not more than 3½ feet (1 m) above the floor
Clearance betwee bottom of the extinguisher and the floor should never be less than 4 inches (100 mm)

## Slide 121: Physical environment is very important to extinguisher reliability.
Greatest concern is the temperature of the environment
Water-based extinguishers
Specialized extinguishers
Must be located where freezing is not possible
Available for temperatures as low as -65°F (-54°C)
Extinguishers using plain water can be provided with antifreeze recommended by the manufacturer

## Slide 122: Understand environmental factors that can impact extinguisher reliability.
Corrosive atmosphere
Outdoor installations
Marine applications
May be present not only in an industrial environment but also in marine applications where extinguishers are exposed to saltwater spray
Extinguisher can be protected with a plastic bag or placed in a cabinet
Extinguishers are available that have been listed for use in a saltwater environment
Courtesy of Tyco Products

## Slide 123: REVIEW QUESTION
What should properly placed fire extinguishers exhibit?

## Slide 124: REVIEW QUESTION
How does an inspector determine if an extinguisher is operational and ready for use?

## Slide 125: Summary
Special-agent extinguishing systems and portable fire extinguishers are major components of fire and life safety systems.
(Cont.)

## Slide 126: Summary
This chapter provided the fire inspector students on both levels with an overview of the types of special-agent systems and portable fire extinguishers that might be found during a building or facility fire inspection.
(Cont.)

## Slide 127: Summary
The inspector should become familiar with the specific types of special-agent fire extinguishing systems that are found locally as well as the locally adopted codes and standards that govern the distribution and installation of portable fire extinguishers.