## Slide 1
Fire Inspection and Code Enforcement
8th Edition Inspector II
Chapter 4 — Construction Types and Occupancy Classifications

## Slide 2: Learning Objective 1
Identify multiple-use occupancies.

## Slide 3: Multi-use occupancies are more complicated to classify.
Which parts of the facility fall under which occupancy
During inspection
Determinations required
Examine occupancy certificates or inspection reports
Verify which occupancy classifications have been assigned
In most cases, only need to verify that the structure still falls under the same classification
If a change is found, consult the building official
(Cont.)

## Slide 4: Multi-use occupancies are more complicated to classify.
Code requirements
In general, NFPA®101® does not require separation of occupancies in the same structure
Local codes may require separations

## Slide 5: Two situations are of particular importance to inspectors.
Different uses in distinctly different portions of the building
Different uses in an intermingled manner that make it impractical to separate for different classifications

## Slide 6: Intermingled use represents a significant challenge for inspectors.
NFPA® 101®
ICC®
Recommends most restrictive requirements
All requirements for one type of occupancy may take precedence
Various requirements from each of the two occupancies will be used
Does not have a separate occupancy classification for multiple-use occupancies
Recognizes structures may have two or more occupancy types
Canada
Canadian codes require separations between these occupancies in most instances
Restrict combinations of occupancies when a high-hazard occupancy is involved

## Slide 7: Inspectors need to understand the concept of incidental use.
Any area designated as incidental use must conform to the occupancy requirements of the building or portion of the building it occupies
ICC®
Fire separation walls, assemblies, or protection must conform to the requirements for the primary use group
Incidental use occupancies
Furnace rooms
Parking garages
Incinerator rooms
Labs/Shops
Waste and linen collection rooms over 100 square feet (9.3m2)

## Slide 8: Model codes usually require fire-resistance-rated separations regarding incidental use.
System without a fire barrier can be installed where permitted
Construction features must separate the rest of the building from the incidental-use area
Must be capable of restricting the passage of fire
Automatic fire extinguishing system
(Cont.)

## Slide 9: Model codes usually require fire-resistance-rated separations regarding incidental use.
Partitions
Must extend from the floor of the use area to the bottom of a fire-resistance-rated floor or ceiling above
Doors leading into these areas must be self-closing or the automatic-closing type that closes when the fire alarm is activated
Doors leading to the areas must meet the provisions outlined in NFPA®80, Standard for Fire Doors and Other Opening Protectives

## Slide 10: Structures containing multiple occupancy types are considered to be mixed-use occupancies.
Each structure is individually classified by its primary occupancy classification
Separated from the other occupancies by the appropriate fire wall separation
Automatic fire suppression system may reduce the fire-resistance rating requirements
Some occupancy classifications are not permitted to share the same building, regardless of fire protection features

## Slide 11: ICC® further divides mixed occupancies.
Accessory
Nonseparated
Separated

## Slide 12: Know the characteristics of accessory structures.
Subsidiary to the main occupancy of a structure
Limited to no more than 10 percent of the area of the story on which they are located
Does not include accessory assembly occupancies that are less than 750 square feet (70 m2) that remain as part of the main occupancy classification
Assembly areas that are accessory to ICC® Group E Educational Occupancies are not considered separate
Except when applying the code’s assembly occupancy requirements like cafeterias attached to schools
(Cont.)

## Slide 13: Know the characteristics of accessory structures.
Group H High-Hazard Groups H-2, H-3, H-4, or H-5 Occupancies must be separated from all other occupancies
Other occupancy types do not require separation except for particular requirements of the individual classification
Examples of accessory uses
Storage area accessory to an office building
Office area accessory to a manufacturing area
Sales area accessory to a storage area

## Slide 14: Know the characteristics of nonseparated occupancies.
Buildings or portions of buildings that have two or more occupancy uses
Each classified according to its own use
ICC® provisions regarding high-rises and fire protection systems are applied to the entire structure

## Slide 15: Know the characteristics of separated occupancies.
Entire structures or portions of structures that have several occupancy types contained within them
Adopted fire code restrictions are applied separately, not to the structure as a whole
Each occupancy complies with adopted fire code requirements for its occupancy type
Separation between each of these occupancies is defined in the ICC® codes
(Cont.)

## Slide 16: Know the characteristics of separated occupancies.

## Slide 17: REVIEW QUESTION
What are the different types of multiple-use occupancies?

## Slide 18: Summary
An inspector’s ability to determine the construction type and occupancy classification of a structure is a critical part of an inspection.
The appropriate occupancy classification must be assigned during the plans review process and verified when the certificate of occupancy is issued before the owner/occupant takes possession of the structure.
(Cont.)

## Slide 19: Summary
    Model building and fire codes provide the inspector with the guidelines for ensuring that life safety requirements are met.
Because the information in this chapter is general in nature, inspectors must become familiar with their locally adopted codes.