## Slide 1
Fire Inspection and Code Enforcement
8th Edition Inspector II
Chapter 5 — Building Construction

## Slide 2: Learning Objective 1
Identify the different types of structural systems used in building construction and the fire risks associated with each.

## Slide 3: Inspectors need to understand structural systems.
Basic structural components are of little value unless they can be assembled into a composite system that will support a building
Construction types and basic structural systems are related

## Slide 4: Construction classification types result from the materials and structural systems used in buildings.
Reinforced concrete or protected steel framing is typical of Type I, fire-resistive buildings
Unprotected steel in a Type I building results in a building being classified as a Type II, noncombustible building
Wood and masonry together are found in ordinary (Type III), heavy-timber (Type IV), and wood frame (Type V) construction

## Slide 5: An inspector must keep in mind that these relationships are not absolute.
Masonry curtain walls can be found in a building with a steel frame
Unprotected steel beams can be used to support a concrete slab
Courtesy of Ron Moore and McKinney (TX) Fire Department

## Slide 6: Basic structural systems can be used in various combinations.
Possible to use both reinforced concrete and a steel frame, or steel and masonry, for different parts of the building
Structural design involves blending the properties of one or more construction materials into a unit that will withstand the forces applied to it in a reliable, economical, functional, and attractive manner

## Slide 7: Inspectors need to know what to look for when evaluating structures.
Refer to the building department or permit office
Construction documents that were submitted with the original building permit
Fire department inspection files
May contain a description of the construction system used
Frequently, all that an inspector can do is to become familiar with prevailing construction methods in the jurisdiction

## Slide 8: Know general types of structural systems.
Bearing wall structures
Loads
Shell and membrane structures
Frame structural systems
Wood structural systems
Masonry structural systems
Steel structural systems
Concrete structural systems

## Slide 9: Know the characteristics and uses of bearing wall structures.
Use the walls of a building to support spanning elements including beams, trusses, and precast concrete slabs
Provide lateral support to the structure along the direction of the wall
Usually exterior walls, but interior walls can provide structural support
Walls are subjected to compressive loads
May be continuous or interrupted for door and window openings
Courtesy of Ron Moore and McKinney (TX) Fire Department

## Slide 10: Inspectors need to be familiar with materials used for bearing wall structures.
Concrete blocks
Bricks
Stone
Concrete panels
Wood

## Slide 11: Inspectors need to know the two types of gravitational forces on buildings.
Dead loads
Live loads
(Cont.)

## Slide 12: Inspectors need to know the two types of gravitational forces on buildings.
Dead loads
Fixed in location
Accurately quantifiable
Weight of any permanent part of a building, including weight of building components
Usually remain the same, but they can change
(Cont.)

## Slide 13: Inspectors need to know the two types of gravitational forces on buildings.
Courtesy of Ed Prendergast
Live loads
Any load that is not fixed or permanent like building contents, occupants, snow/rain
Usually the actual weight and distribution of contents are not known exactly
Vary by occupancy
Building codes specify minimum live loads to be used in the design process

## Slide 14: Be familiar with some of the uniformly distributed live loads required by the IBC.

## Slide 15: Inspectors need to know the characteristics of a concentrated load.
A concentrated load is one that is applied at one point or over a small area
Produce high localized forces and non-uniform loads in the supporting structural members
Building codes require that a specified minimum concentrated load be used in the structural analysis when it creates greater load effects than the uniform load

## Slide 16: REVIEW QUESTION
What are the forces on a building as a result of gravity called?

## Slide 17: Learn the characteristics of shell and membrane structures.
Fabric has long been used for tents or other temporary shelters
Newer fabrics can be used as part of walls and roofs of permanent structures
Consist primarily of an enclosing, waterproof surface
Stresses resulting from applied loads occur within surface bearing wall structures
(Cont.)

## Slide 18: Learn the characteristics of shell and membrane structures.
Air-supported structures are supported by the pressurization of the entire surface inside
Building codes typically address membrane structures with a life of 180 days or more
Fire codes address those used for fewer than 180 days
Membrane structures are permanent; tents are temporary

## Slide 19: Understand the design advantages of membrane structures.
Can usually be erected in less time than a rigid structural system
Fabric can flex and absorb some of the stresses from seismic and wind forces
Fabric also permits the development of innovative architectural shapes
Fabrics weigh less than other roof systems

## Slide 20: Understand the disadvantages of membrane structures.
Must be supported by cables and masts or a tubular framework
Support system must provide sufficient rigidity to avoid shaking or flapping
Fabrics cannot be used to support building appliances
When an automatic sprinkler system is required, the piping must be supported from the framework
Fabrics are considerably thinner than other assemblies used for roof systems; sometimes two layers are used; space between creates a thermal barrier

## Slide 21: Become familiar with the materials used in membrane structures.
Must be noncombustible or must meet the fire propagation performance requirements in the locally adopted code
Can also be used in fire-resistive construction when a building code only requires a noncombustible roof for a fire-resistive building

## Slide 22: REVIEW QUESTION
What are some of the advantages of membrane structures?

## Slide 23: Know the characteristics of frame structural systems.
Structural support is provided in a manner similar to the way the skeleton supports the human body
Walls act as the "skin" to enclose the frame
Walls may also provide lateral stiffness but provide no structural support
In the fire service, the term frame construction often refers to a wood-frame building
Frame structural systems are also built using other materials

## Slide 24: Learn the characteristics of steel stud wall framing.
Courtesy of Ed Prendergast
Relatively closely spaced vertical steel studs connected by top and bottom horizontal members
Historically associated with use of wood studs
Use of steel studs has become more common in recent years
Frequently provided with diagonal bracing for stability
Both sides may be covered with paneling and sheathing

## Slide 25: Become familiar with post and beam framing.
Posts support the beams that are subject to transverse loads
Evolved from use of tree trunks for framing
Commonly associated with wood beams and columns
Other materials can be used
Distinctive characteristic is the spacing of vertical posts and cross-sectional dimension of the members
Requires addition of other members to withstand lateral loads

## Slide 26: Inspectors need to know about truss frames.
Can be adapted to a variety of applications
Possible to build components of a frame using a series of trusses

## Slide 27: Inspectors should understand slab and column frames.
Most frequently encountered in concrete structures
Floor slabs in multistory, reinforced-concrete buildings are supported by concrete columns
Other horizontal systems that can be used to support floor loads include wood decks and metal decks supported by beams and columns

## Slide 28: Inspectors need to be familiar with rigid frame structural systems.
Courtesy of Ron Moore and McKinney (TX) Fire Department
Used when joints between a column and a beam are reinforced so bending stresses can be transmitted through the joints
Easily recognized in single-story, gabled-roof and rigid-frame buildings
Used in other types of structures including multistory and multispan designs
Joints will be the last portion of the assembly to fail under fire conditions

## Slide 29: REVIEW QUESTION
What are the different types of frame structural systems?

## Slide 30: Wood structural systems are almost always used in Type IV and Type V construction.
Interior and exterior framing
One- and two-family dwellings
Townhouses
Apartment buildings
Hotels of five stories or less

## Slide 31: Wood framing systems most frequently encountered are classified into three basic types.
Wood framing (Type V)
Post and beam framing
Heavy-timber framing (Type IV)

## Slide 32: The most popular form of wood framing is known as wood-frame construction.
Walls are formed from vertical members known as studs
Floors are supported by joists or trusses
Inclined roofs are supported by rafters or light trusses

## Slide 33: There are two common types of wood framing.
Balloon framing
Platform framing

## Slide 34: Wood framing is usually covered with an interior finish of plaster or drywall.
Courtesy of Ron Moore and McKinney (TX) Fire Department
Will act to retard the spread of fire into the stud spaces
If a fire originates in the stud space or spreads into it, it can readily spread from the vertical cavity into the horizontal joists and attic space
Fire-stopping must be provided in addition to the structural members

## Slide 35: Inspectors need to recognize the characteristics of platform framing.
Courtesy of Ed Prendergast
Exterior wall vertical studs are not continuous
First floor is constructed as a platform upon which exterior vertical studs are erected
Second-story framing is erected on the platform formed by the story joists and flooring
The plate installed on the top of the studs provides a fire-stop that tends to block spread of fire from floor to floor within the walls

## Slide 36: Inspectors need to recognize the characteristics of balloon framing.
Uses closely spaced members (studs) that are continuous from the sill to the top plate of the roof line
Joists that support the second floor are nailed directly to the studs
Vertical combustible spaces between the studs provide a channel for rapid communication of fire from floor to floor
Courtesy of Wil Dane

## Slide 37: Inspectors need to recognize the characteristics of heavy-timber framing.
Courtesy of Ed Prendergast
Basic structural support is provided by a framework of beams and columns
Ordinary corrugated sheet metal is sometimes used for exterior walls of small buildings
Exterior walls may be non-load-bearing panels with an exterior siding that may be any of several materials
Interior wood surface is usually left exposed, which eliminates combustible voids and creates a rustic finish

## Slide 38: REVIEW QUESTION
Where are you most likely to find wood structural systems as interior and exterior framing?

## Slide 39: Inspectors need to understand masonry structural systems.
Courtesy of Ron Moore, McKinney (TX) Fire Department
Used to construct bearing walls that provide the basic structural support for a building
Can be used for non-load-bearing curtain walls or partition walls
Exterior walls are used with a variety of framing systems including unprotected steel, protected steel, and wood
Both fire-resistive and non-fire-resistive buildings may feature masonry walls

## Slide 40: Inspectors need to be familiar with masonry wall construction.
Masonry units are laid side by side in a horizontal layer known as a course
Horizontal courses of brick are laid on top of each other in a vertical layer known as a wythe
Simplest brick wall consists of a wall with a single wythe
Multiple wythes are commonly used to supply the necessary strength and stability

## Slide 41: Other brick placements are made for appearance or strength.
Stretcher course
Bricks placed end-to-end
Soldier course
Bricks placed vertically on end
Header course
Bricks placed with the end facing out

## Slide 42: Several elements contribute to the strength and stability of plain (nonreinforced) masonry walls.
Weight of the masonry
Horizontal bonding between adjacent wythes
Vertical compressive strength of the masonry units
Corrosion-resistant metal ties provide horizontal bonding

## Slide 43: Exterior brick walls usually have a vertical cavity between the exterior and interior wythes.
Prevents seepage of water through mortar joints
Increases thermal insulating value of the wall
Placement of metal ties is important because the use of a brick header course usually is not practical

## Slide 44: Inspectors need to understand structural stability in masonry structural systems.
Placing vertical steel rods in a cavity between two adjacent wythes of a brick wall effectively reinforces walls
Cavity is filled with grout
As the height of a wall is increased, the thickness of the wall at the base must be increased as the load-bearing area of the wall increases
(Cont.)

## Slide 45: NOTE
Placing the steel rods in the openings in the individual blocks and filling the opening with grout reinforces concrete block walls in a similar manner.

## Slide 46: Inspectors need to understand structural stability in masonry structural systems.
Disadvantages
Increasing weight of a load-bearing wall with increased height makes very tall masonry structures impractical or more costly than alternative designs unless the masonry is reinforced with steel
Reinforcement method
Extending tension rods through the masonry walls; attaching them to thrust plates on the outside
Thrust plates are usually visible on the outside; may indicate that the building has undergone repairs
Courtesy of Dave Coombs

## Slide 47: Inspectors need to be familiar with interior structural framing.
Courtesy of Dave Coombs
Can include a combination of unprotected steel, protected steel, and wood
Joists, beams, or trusses are used to transfer the gravity load of the building contents
Masonry buildings with wood interior framing are classified as ordinary (Type III), heavy-timber (Type IV)
Classification depends on size of the wooden structural members

## Slide 48: Inspectors need to be familiar with the fire resistance of masonry walls.
Depends on the type of masonry units used and the thickness of the wall
As the thickness of a masonry wall increases, generally the fire resistance increases
Building codes usually permit less clearance (separation) between buildings with masonry or other fire-resistive exterior walls
Less likely to communicate fire from structure to structure

## Slide 49: REVIEW QUESTION
What is one method of reinforcing a masonry structure?

## Slide 50: Know the characteristics of steel structural systems.
Courtesy of Ron Moore, McKinney (TX) Fire Department
Primary material used for structural support in the construction of large modern buildings
Can be used to construct a frame of columns, beams, and girders
Can be used in heavy or lightweight trusses to support roofs and floors
Rigid frames and arches can be constructed from steel
Steel cables or rods can be used to support roofs
Cold-rolled steel studs are being used to construct exterior walls
(Cont.)

## Slide 51: Know the characteristics of steel structural systems.
Courtesy of Ron Moore, McKinney (TX) Fire Department
Steel is a strong but very dense material
Not efficient to use it in the form of solid slabs or panels
Steel in sheet form, however, is used for applications such as floor decking and exterior curtain walls
Exterior envelope of a steel-frame building can consist of concrete, masonry, or glass
Can be fabricated in a variety of shapes
Frequently used in three-dimensional space frames
Can also be constructed of wood or a combination of steel and wood

## Slide 52: REVIEW QUESTION
In what type of structure are you most likely to find steel structural systems?

## Slide 53: Know the most common uses for concrete structural systems.
Foundation stem walls
Floor slabs
Driveways
Walks

## Slide 54: Know the other uses for concrete structural systems.
Interior and exterior walls
Roof decks
Floors of upper stories
Stairways
Elevated walkways
Roof tiles
Decorative interior finish

## Slide 55: Know some of the characteristics for concrete structural systems.
May be precast
May be cast-in-place
May be the construction system for entire structures

## Slide 56: Inspectors need to understand the characteristics of cast-in-place concrete.
Courtesy of Ron Moore, McKinney (TX) Fire Department
Permits designer to cast the concrete in a wider variety of shapes
Does not develop its design strength until after it has been placed where it will be cured and used

## Slide 57: Inspectors need to understand precast concrete.
Courtesy of Dave Coombs
Placed in forms and cured at a precasting plant away from the job site
Transported to the job site and hoisted into position
Buildings can be built using whole precast modular units
Precast parts assembled into a framework for the building are more common
More in common with steel-framed buildings than with cast-in-place concrete buildings

## Slide 58: Inspectors need to know how concrete structural systems are reinforced.
Steel bars are placed in the formwork
Concrete must be properly compacted as it is placed in the forms to completely surround the rebars
Wet concrete is placed in the formwork around the bars
When hardened, it adheres to the reinforcing bars because of textural shaping on the surface of the bars
Courtesy of Dace Prendergast

## Slide 59: More efficient use of concrete is made by either pretensioning or posttensioning the concrete.
Needed when a concrete beam or floor slab supports a load
Both processes use the same basic materials
(Cont.)

## Slide 60: More efficient use of concrete is made by either pretensioning or posttensioning the concrete.
Pretensioned reinforcement
Uses steel strands stretched between anchors producing a tensile force in the steel
Concrete is then placed around the steel strands and allowed to harden
Once hardened, the force applied to the steel strands is released
Strands exert a compressive force in the concrete
(Cont.)

## Slide 61: More efficient use of concrete is made by either pretensioning or posttensioning the concrete.
Courtesy of McKinney (TX) Fire Department
Post-tensioned reinforcement
Uses reinforcing steel that is not tensioned until after the concrete has hardened
Reinforcing strands are placed in formwork; covered with grease or a plastic tubing to prevent binding
Jack is used to apply a large tensile force to the steel that stretches the steel and results in a compressive force in the concrete
Reinforcing cables are trimmed to the edge of the concrete and grouted
(Cont.)

## Slide 62: More efficient use of concrete is made by either pretensioning or posttensioning the concrete.
Difficult to determine which type of reinforcing has been used in a concrete frame building
May be impossible to distinguish between cast-in-place concrete and precast concrete after a building is completed
Some systems such as stucco and EIFS may appear to be concrete

## Slide 63: REVIEW QUESTION
What can concrete structural systems be used for in building construction?

## Slide 64: Summary
The type of construction determines the needed protection systems and structural separations that some occupancy classifications require.
The building materials and the structural systems are components of the specific building type and will add to or subtract from the fire-resistive nature of the building.
(Cont.)

## Slide 65: Summary
The inspector must have a strong working knowledge of these building elements and how they reduce risk in case a fire does occur.