## Slide 1
Fire Inspection and Code Enforcement
8th Edition Inspector II
Chapter 6 — Building Components

## Slide 2: Learning Objective 1
Describe the characteristics of fire walls.

## Slide 3: Understand the characteristics of fire walls.
Subdivide a building into smaller areas
Freestanding fire walls are self-supporting; independent of the building frame
Tied walls require support from the surrounding structure; often lighter; may be double-wall
Can also separate various functions within a structure
Can be constructed as freestanding walls or tied walls
(Cont.)

## Slide 4: Understand the characteristics of fire walls.
Structural members
Must have sufficient strength to resist the lateral pull of collapse on either side
No combustible structural members may penetrate
Must have the same degree of fire resistance as that required for the fire wall
Combustible members
If framed into a fire wall, they must be designed to fall away freely from the wall under fire conditions

## Slide 5: Inspectors need to be familiar with compartmentation systems.
When the floor area of a building is subdivided with fire-resistive partitions or walls, it is said to be compartmentalized or part of a compartmentation system
(Cont.)

## Slide 6: Inspectors need to be familiar with compartmentation systems.
Fire-rated partitions or fire barriers
Not self-supporting and free-standing like fire walls
Openings
Designed to contain fire to one area
Protection of openings
Doors, windows, access panels
Fire doors
Nullify the value of the partitions unless protected
Shutters
Other rated building components

## Slide 7: REVIEW QUESTION
What are some of the common characteristics of fire walls?

## Slide 8: Learning Objective 2
Describe the hazards solar panels pose for firefighters.

## Slide 9: Inspectors need to understand rooftop photovoltaic systems.
Courtesy of McKinney (TX) Fire Department
Recent technological advancements, increased energy costs have created a market
Convert energy from the sun into usable electricity
Can be found on both residential and commercial buildings
Provide electrical power to the building
Commonly referred to as solar panels
Sends electricity into the public utility grid; can provide rebates to owners

## Slide 10: Understand the hazards of rooftop photovoltaic systems for firefighters.
Can generate up to 8 amps and 600 volts of electricity
During a daytime fire, the system may continue to produce electricity
(Cont.)

## Slide 11: Understand the hazards of rooftop photovoltaic systems for firefighters.
Disconnect switch prohibits the electricity from the switch to the structure’s main electrical system
All conduit and system disconnect switches should be marked according to model codes
Electricity between the PV panels and the disconnect switch continues

## Slide 12: Know requirements for access pathways and smoke ventilation for solar panel systems.
Systems are designed to produce the maximum amount of electricity they can
Design is a problem for firefighters to access/egress pathways to and on a roof
Once on the roof, areas must be provided for smoke ventilation operations
Model building codes have criteria for the paths and ventilation points
Conversations with the responding fire fighting support companies could be beneficial before a fire occurs
More PV panels mean more electricity

## Slide 13: REVIEW QUESTION
What are the hazards solar panels pose for firefighters?

## Slide 14: Learning Objective 3
Identify the standardized testing method currently accepted by building codes.

## Slide 15: Inspectors need to be familiar with the ASTM E-119 test.
Only standardized test method currently universally accepted by building codes
Evaluates the ability of structural assemblies to carry a structural load and to act as a fire barrier

## Slide 16: Inspectors need to understand the limitations of the ASTM E-119 test.
Information about performance of assemblies constructed with components or lengths other than those tested
Evaluation of the extent to which the assembly may generate smoke, toxic gases, or other products of combustion
Measurement of the degree of control or limitation of the passage of smoke or products of combustion
(Cont.)

## Slide 17: Inspectors need to understand the limitations of the ASTM E-119 test.
Fire behavior of joints between building elements such as floor-to-wall or wall-to-wall connections
Measurement of flame spread over the surface of the tested material
(Cont.)

## Slide 18: Inspectors need to understand the limitations of the ASTM E-119 test.
Effect on fire endurance of openings in an assembly
Electrical outlets and plumbing openings
When the continuity of an assembly is destroyed, it cannot function as a fire barrier
Fire-resistive assemblies may be penetrated
Penetrations may be made for ductwork, plumbing, electrical, or communication purposes
May not be adequately firestopped

## Slide 19: Inspectors need to understand the most important limitation of the ASTM E-119 test.
Particular interest to building and fire prevention inspectors
Over time, and particularly during renovation, fire-resistive assemblies may be penetrated
Penetrations may be made for ductwork, plumbing, electrical, or communication purposes
When the continuity of an assembly is destroyed, it cannot function as a fire barrier
Penetrations may not be adequately firestopped

## Slide 20: REVIEW QUESTION
List the information that cannot be obtained from E-119 standard testing.

## Slide 21: Learning Objective 4
Describe the characteristics of interior components to be evaluated during fire inspections.

## Slide 22: Know what an Inspector II evaluates when it comes to interior components.
Floor finishes
Ceilings
Stairs

## Slide 23: Floor finishes are classified by the amount of heat that can be applied before ignition and fire spread.
Two classes of floor finishes: Class I and Class II
Class I can withstand higher temperatures
Generally, the exits, exit passageways, and corridors require Class I interior floor finishes
Automatic sprinkler system will decrease the requirement to Class II
The more critical the fire exposure, the higher the classification required

## Slide 24: Understand what ceiling components and materials need to be evaluated.
Materials can be attached directly to the underside of floor joists or trusses
Common for old buildings to have a new ceiling installed below an existing ceiling
Space above the ceiling, called interstitial, can be used to conceal ducts, wiring, piping, etc.
Verify wires, ducts, pipes, etc. are noncombustible or rated for plenum use
Materials can be installed at a distance below the floor supports, creating a large concealed space
Ceiling materials can conceal the type of floor or roof structure above
Courtesy of Ron Moore, McKinney (TX) Fire Department

## Slide 25: Understand what stair components and materials need to be evaluated.
Access or convenience stairs are not required to be a part of the means of egress system; typically connect no more than two levels
Can be classified as either interior or exterior
Stairs meeting these requirements are called protected or enclosed
Stairs that are a part of the required means of egress must be evaluated so occupants can travel to safety
Fire escapes, escalators, and fixed ladders are no longer allowed as components in the required means of egress
(Cont.)

## Slide 26: Understand what stair components and materials need to be evaluated.
The slide escape was another device used for some time that is no longer permitted for newly constructed buildings

## Slide 27: REVIEW QUESTION
What are some of the characteristics of interior components an Inspector II should be prepared to evaluate?

## Slide 28: Learning Objective 5
Explain the inconsistencies in fire door classifications.

## Slide 29: Recognize the inconsistencies in regards to fire door classifications.
Use locally adopted code
Code may permit an opening in a 2-hour-rated stairwell enclosure
Code may require two 3-hour-rated fire doors to protect an opening in a 4-hour-rated wall
1/3-hour-rated door may be found being used as a smoke barrier and an opening to a corridor
Openings need to be protected with a 1½-hour-rated fire door rather than a 2-hour-rated door
May not permit a 3-hour-rated door to be used in combination with a 1½-hour-rated door to satisfy the requirement

## Slide 30: NOTE
The reason for a difference between the rating of a fire door and a fire-rated wall is that the test criteria for the two are different.

## Slide 31: REVIEW QUESTION
Provide an example of an inconsistent door classification.

## Slide 32: Learning Objective 6
Identify the testing methods used to evaluate interior finishes.

## Slide 33: Understand the evaluation of interior finishes.
Flammable interior finishes can intensify fires
Fire-retardant coatings have also been developed, tested, and approved
UL and other organizations developed testing methods to establish flame-spread ratings
Ratings based on smoke development were also developed
(Cont.)

## Slide 34: Understand the evaluation of interior finishes.
Be aware that modifications to buildings can affect a component’s fire rating
Modifications or repairs should conform to the same level that was originally approved
Research original plans to determine these fire ratings

## Slide 35: Become familiar with the Steiner Tunnel Test.
Most commonly used method
Numerical evaluation of the flammability of interior materials
Flame spread rating
Smoke developed index
For evaluating surface-burning characteristics

## Slide 36: Inspectors need to understand flame spread rating.
Means of comparison
Building codes
Classifications
Under controlled test conditions
Red oak flooring is the standard; all materials are tested against it
Use the ratings to establish some control over interior finishes
Three classifications for interior finishes
Used to establish control material uses in occupancies
Red oak flooring is assigned a rating of 100
(Cont.)

## Slide 37: Inspectors need to understand flame spread rating.
(Cont.)

## Slide 38: Inspectors need to understand flame spread rating.

## Slide 39: Inspectors need to understand the limitations of flame spread ratings.
Not an absolute measure
Floor coverings
Room shape and dimensions and fuel load within the compartment have a significant effect
Differences between field applications and test conditions create a differing behavior in the field
Does not apply
Application differences
However, if used for a wall or ceiling finish, it must meet the same flame spread criteria as other wall and ceiling finishes
(Cont.)

## Slide 40: Inspectors need to understand the limitations of flame spread ratings.
No way that flame spread ratings can be positively determined in the field
Relative surface burning can be assumed for some interior surfaces, such as concrete block or plaster
Other materials can usually be assumed to have a higher flame spread rating
Ratings of many materials cannot be determined in the field unless the manufacturer can be identified and contacted

## Slide 41: Inspectors need to understand the smoke-developed index.
Another measure of flammability
Measure of the relative visual obscurity created by the smoke from a tested material
Measured by means of a photoelectric cell and a light source located at the end of the tunnel furnace
Red oak is used as a standard; assigned rating of 100

## Slide 42: Inspectors need to understand the limitations of the smoke-developed index.
Not an indication of the toxicity of products of combustion of interior finish materials
Will not detect or measure a completely transparent product of combustion such as carbon monoxide
Does not measure the combined effects of heat, irritation, and toxicity

## Slide 43: Fire-retardant coatings can reduce flame spread ratings of some interior finishes.
Types of coatings
Intumescent paints
Behaviors
Intumescent paints expand upon exposure to heat to create a thick, puffy coating
Mastics
Cementitous (cement-based) and mineral-fiber coatings
Topical fire-retardant coatings
Mastic coatings form a thick, noncombustible membrane over the surface
Limits
Only effective when applied as directed
Susceptible to misuse

## Slide 44: CAUTION
Fire-retardant coatings only affect the material’s surface. In addition, a material that is listed as a fire-retardant coating does not increase the fire resistance of structural components or assemblies unless it has also been tested and listed for use in a fire-resistive assembly. However, because fire-retardant coatings can be field-applied, contractors and design professionals may attempt to substitute them as an inexpensive remedy for other fire protection shortcomings.

## Slide 45: REVIEW QUESTION
What are the common testing methods used to evaluate interior finishes?

## Slide 46: Learning Objective 7
Describe building service characteristics that require inspector evaluations.

## Slide 47: Evaluating building services is a part of an inspector’s job.
Buildings contain a variety of services and subsystems
All services and subsystems can impact fire and life safety
Must be appropriately designed, installed, inspected, tested, and maintained
Designed to provide safety, convenience, and comfort for occupants
Defective subsystems can have detrimental effects on the entire system
(Cont.)

## Slide 48: Evaluating building services is a part of an inspector’s job.
Inspector’s responsibility
Verify that the designer and owner have installed and maintained building services in compliance with the locally adopted fire and life safety building codes

## Slide 49: HVAC systems have several purposes.
Designed primarily for occupant comfort
Regulate intake of outdoor air and recirculation of indoor air

## Slide 50: Inspectors should verify that HVAC equipment is properly maintained.
Reviewing maintenance records
Conducting field observations

## Slide 51: Verify documentation of regular maintenance of several HVAC systems.
Outside air intakes
Fans
Air filtration devices
Exhaust properly sealed into chimneys
Air heating and cooling equipment
Air ducts
Smoke/fire dampers
(Cont.)

## Slide 52: Verify documentation of regular maintenance of several HVAC systems.

## Slide 53: Codes may require the installation of smoke or fire dampers.
Smoke dampers
Usually actuated by an associated smoke detector; may be actuated by an automatic signal from the building fire alarm system
Protect duct penetrations through fire-rated assemblies
Usually a spring-loaded shutter
Held open by a fusible link
Combination smoke and fire dampers
Close in response to heat or smoke
Protect duct penetrations through fire-rated assemblies
Usually closes by active mechanical action
Fire dampers

## Slide 54: Know additional codes requirements for HVAC systems.
Internal duct smoke detection devices
Automatically turns off the system
Most codes require them
Intent is to prevent the system from spreading and recirculating smoke
Should never be considered a substitute for area smoke detectors

## Slide 55: Most buildings use a system of passive smoke control to prevent smoke from traveling through the system.
Fire detected, HVAC system fan deactivates
Dampers activate at points where the HVAC ducts pass through smoke or fire-barrier walls
Compartmentalizes the fire
Dampers should be inspected by a qualified person and also exercised

## Slide 56: Smoke detectors can be located in several places in an HVAC system.
Main supply ducts
Downstream of the air filters and cleaners
Return air ducts
Locations depend on the mechanical building code under which they were installed

## Slide 57: HVAC systems can be used for active smoke control.
Air is drawn from the fire area and discharged to the outside
Fire dampers are usually omitted
Common in covered malls, underground buildings, and high-rises
Return air supply to all or part of the building ceases
(Cont.)

## Slide 58: HVAC systems can be used for active smoke control.
Lengthy time for evacuation
Aerial ladders cannot reach upper floors
Strong air-flow patterns are found in vertical shafts
Important in underground structures where exit travel is into upper floors
Must be capable of maintaining smoke- and heat-free exit route
Must be designed to allow for sufficient evacuation time for occupants

## Slide 59: The National Building Code of Canada (NBC) identifies 14 different methods of smoke control in buildings.
Inspector must verify
Measures do not include smoke-control measures that have been implemented as equivalent methods or alternatives permitted by objective-based codes
Be familiar with the testing requirements and the frequency for testing these systems
Always request documentation that the required testing and maintenance has been performed by a qualified person

## Slide 60: Be familiar with building refrigeration systems.
Installed in buildings to add or remove heat
Controls the air temperatures for heating and cooling
In commercial buildings, these systems are also used to
Preserve foods
Maintain the temperature of pharmaceuticals
Ensure that certain hazardous materials do not become unstable
Building occupants
Processes/items

## Slide 61: Inspectors require a basic understanding of the ASHRAE standard.
ASHRAE (American Society of Heating, Refrigeration and Air Conditioning Engineers)
ASHRAE Standard 34, Designation and Safety Classifications of Refrigerants, is used to classify refrigerants
Amount of refrigerant in the system and its classification dictate when the jurisdiction's fire code requirements for these systems are applicable
ASHRAE 34 uses an alphabet-numerical system for classification of refrigerants
(Cont.)

## Slide 62: Inspectors require a basic understanding of the ASHRAE standard regarding health hazards.
Type B refrigerants are more toxic
Type A refrigerants are less toxic than Type B

## Slide 63: Inspectors require a basic understanding of the ASHRAE standard regarding flammability.
Class 1 refrigerants
Noncombustible
Class 3 refrigerants
Flammable

## Slide 64: Model codes require refrigeration machinery rooms to be equipped with gas detection systems.
Courtesy of Scott Stookey, International Code Council, Washington DC
Used to alert facility personnel of possible refrigerant leaks
Must activate occupant notification devices
Alarm must be transmitted to an approved location

## Slide 65: Model codes also require mechanical ventilation systems in refrigeration machinery rooms.
Codes require this system to provide a means of exhausting the room in the event of a refrigerant leak
Activated by the gas detection system

## Slide 66: Codes require a manual means of controlling the previous safety systems in an emergency.
Courtesy of Scott Stookey, International Code Council, Washington DC
Used if the gas detection or mechanical ventilation system fails to operate
Model fire codes require a break-glass type switch near the machinery room in an approved location
Switch should shutdown compressors, pumps and automatic valves
Second emergency switch is required to manually activate the mechanical ventilation system

## Slide 67: Refrigerant hazard information must be clearly identified.
Courtesy of Scott Stookey, International Code Council, Washington DC
Must post health, flammability and instability hazards
Model fire codes require signs that comply with NFPA® 704, Standard System for the Identification of the Hazards of Materials for Emergency Response

## Slide 68: Inspectors need to know about electrical systems.
Equipment may be installed in separate rooms, vaults, or separate buildings
May be above or below grade level or on individual floors
Codes may require electrical system components be separated from the rest of the building by fire-rated construction

## Slide 69: All structures that have electrical power systems have electrical service panels.
Distribute electrical power that arrives at the panel into individual circuits
Circuits are designed to
Evenly distribute the electricity
Prevent wiring from becoming overloaded
Ensure adequate power for equipment
Circuit breakers
Turn off power to the circuit if there is a short
(Cont.)

## Slide 70: All structures that have electrical power systems have electrical service panels.
Fuses and fuse boxes
Master control switches
Control all the electricity that enters the panel
These switches/fuses may be used to turn off power to the building
Circuit breakers have replaced fuses
Present within either the circuit breaker or fuse box service panel
However, fuse boxes are still found in structures built before 1950
May still be found on air-conditioning units

## Slide 71: Switch gear is a term used to describe electrical equipment used to isolate circuits and energized equipment.
Where they are found
Electrical power stations
Industrial complexes
Electrical equipment rooms
What they contain
Multiple circuit breakers or switches that will prevent a short in the system or reset it after a short has occurred

## Slide 72: Inspectors need to know the characteristics of generators.
Supply backup power during an emergency
May be limited to operating the fire protection systems and emergency lighting systems
May have the capacity to provide power to the entire building
Natural gas and diesel are the main types of fuel
Generally located outside a building; may also be found in basement areas
Power transfer switch starts the generator when there is a loss of power; turns it off when the primary power supply reengages

## Slide 73: Inspectors need to know the characteristics of transformers.
Characteristics
Some power special systems and equipment in industrial and commercial buildings
Generate heat; air cooling and oil cooling are the two most common cooling methods
Convert high-voltage electricity supplied to an appropriate voltage for use in a building

## Slide 74: Inspectors need to understand the two most common transformer cooling methods.
Air-cooled
Oil-cooled or oil-filled
Use the surrounding air to cool the transformer
Contains oil to conduct heat away from the core and to electrically insulate internal components
Has fins and heat sinks installed on the body
Also called dry transformers
Hazard of being energized electrical equipment
Potential source of a combustible liquid leak

## Slide 75: CAUTION
Be cautious when examining any transformers. Transformer hazards are the same as those with any other energized electrical equipment, especially electrocution or fires caused by shorts, arcs, and sparks.

## Slide 76: Inspectors need to know the characteristics of elevator hoistways.
Can act as a vertical chimney; spread fire and smoke throughout a building
If not vented at the top, the hot gases and smoke may accumulate and spread horizontally to the upper floors
Model building codes require venting at the top of nearly every hoistway built today
(Cont.)

## Slide 77: Inspectors need to know the characteristics of elevator hoistways.
Hoistway enclosures are usually required to be fire-rated assemblies
Any penetrations through the hoistway walls must be done with the installation of an appropriately rated assembly
No wiring, ductwork, or piping should be run within the hoistway unless it is required for the elevator itself

## Slide 78: Inspectors need to know the characteristics of elevator hoistway doors.
Rated assemblies that work in conjunction with the car doors
Same types as car doors with one addition: a swinging door is installed on some hoistways
May not completely prevent the passage of smoke from the hoistway into the building because some door clearance is required for operation
Depend upon the car doors for their power

## Slide 79: Hoistway door assemblies are listed and labeled with a fire-resistance rating.
Fire-resistance rating should be clearly visible on the label, which is on the hoistway side of the door
Assembly must be installed in accordance with the manufacturer’s instructions
Any hardware, such as floor sill, header, and closure equipment, must also be labeled

## Slide 80: The inspector should have knowledge of chases and shafts.
Can provide a vertical path for smoke and fire
Can serve as the area of origin
Vertical shaft enclosures are built with fire-rated construction methods; contain combustible materials
These areas are critical for the inspector to verify that the required firestopping has been installed and maintained

## Slide 81: Refuse and linen chutes are examples of vertical shafts.
Must be constructed of noncombustible material with rated doors
A fire-rated enclosure must surround the chute
Automatic sprinklers may be required at the top of the chute; in its termination room
Poor maintenance or loss of operational integrity can result in some smoke escaping
Be aware of these weak points; evaluate that components are intact

## Slide 82: Know the special concerns regarding manifold grease ducts.
Serve more than one exhaust hood
Duct is smallest as it leaves each single exhaust hood
Typically have separate fire suppression systems for each hood
Each branch duct operates simultaneously for protection of the common duct
Normally found in such areas as food courts in shopping malls
If not properly maintained, fire may spread over large areas within the building
Size increases in cross-section as it joins with another branch duct

## Slide 83: Some exhaust systems have additional grease-removal devices in the duct system.
Known as extractors
May be located in false ceiling spaces, in a mezzanine, or on the roof
May present hazards due to accumulation of grease on filters and fusible links
Some design applications include horizontal ducts

## Slide 84: Grease extraction and control equipment may be installed to remove odors.
Most of this equipment is installed on the roof
Some systems are designed with water wash or odor-control chemical spray systems
May also be located in ceiling spaces
May contain
Filters
Electrostatic precipitators
Catalysts
Odor absorbers
Gas-fired afterburners

## Slide 85: REVIEW QUESTION
What are some of the building service hazards inspectors should be aware of during an inspection?

## Slide 86: Summary
Components that make a building habitable are incorporated into a building’s structural system.
Exterior walls, roofs, and floors enclose the structural components to define a building’s limits.
(Cont.)

## Slide 87: Summary
Within these components, interior walls, floors, and ceilings further divide the space to create individual work and living compartments or rooms.
Stairs, doors, and windows provide access to a structure and between the individual spaces.
(Cont.)

## Slide 88: Summary
    Walls, floors, and ceilings are finished with interior finishes that may or may not contribute to fire spread by increasing or limiting the fuel load of the compartment.
Building services include elevators, HVAC systems, and others that may also increase or decrease the inherent fire hazards within a building.
(Cont.)

## Slide 89: Summary
    An inspector must be able to evaluate these building components and determine the level of fire protection provided by them.