## Slide 1
Fire Inspection and Code Enforcement
8th Edition Inspector II
Chapter 10 — Hazardous Materials

## Slide 2: Learning Objective 1
Describe an inspector's role in process controls.

## Slide 3: Know requirements for hazardous manufacturing processes.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
Regularly use two or more hazardous materials
Model fire codes require systems be properly designed by a competent design professional
If materials are not used properly, they may rapidly decompose and result in a fire or explosion
(Cont.)

## Slide 4: Know requirements for hazardous manufacturing processes.
IFC and NFPA® 400 require that hazardous materials follow a proper path during the manufacturing processes
Inspectors may require a Technical Report and Opinion, prepared by an authorized person, to clarify the process or its potential hazards
Codes require that the process must not exceed the temperature or pressure limits established by the designer

## Slide 5: REVIEW QUESTION
What can an inspector require to clarify processes?

## Slide 6: Learning Objective 2
Identify an inspector's responsibility after an unauthorized discharge.

## Slide 7: Unauthorized discharge is a release of a hazardous material that does not conform to codes and regulations.
As defined by IFC and NFPA® 400
Inspector’s responsibility
A stop-use order may be issued
Work to prevent additional incidents
In some cases, the hazardous material will need to be removed from the system
Plan of action
Consider the required steps so that repairs or improvements can be safely accomplished without creating another incident

## Slide 8: REVIEW QUESTION
What can an inspector do in response to an unauthorized discharge?

## Slide 9: Learning Objective 3
Describe requirements for piping, valves, and fittings that convey hazardous materials.

## Slide 10: IFC and NFPA® 400 have extensive requirements for piping systems design, erection, and testing.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
Components of piping systems that convey hazardous materials from cylinders and tanks to a point of use
Piping systems are required to be constructed of materials with adequate strength and durability and are chemically compatible with the material being conveyed
Model fire codes require hazardous materials piping systems be constructed to ASME B31.3
Verify that the installation matches the approved plans

## Slide 11: Know when codes prescribe the installation of an excess flow control valve or other means of flow control.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
In piping systems conveying flammable, pyrophoric, toxic, and corrosive liquids and gases
Selected based on pipe diameter and material being conveyed
Key inspection issue for excess flow control valves is pipe diameter changes
Excess flow control valves are designed to stop the flow at a predetermined setting or if the pipe is severed

## Slide 12: REVIEW QUESTION
List some of the requirements for piping, valves, and fittings used to convey hazardous materials.

## Slide 13: Learning Objective 4
Recognize the classification system and requirements for hazardous and high-hazard occupancies.

## Slide 14: Hazardous occupancies represent some of the most challenging building uses.
If the amount of hazardous materials in a building exceed the MAQ, IBC and NFPA® 400 require compliance with applicable Hazardous or High-Hazard occupancy classification
Design and construction are based on the classification of hazardous materials that are stored or used
Hazardous occupancies are assigned to one or more of four different categories, based on the physical or health hazards
Classifications change when materials change
Generally, the lower the occupancy number, the greater the hazard the building presents

## Slide 15: Understand Group H-1/High Hazard Level 1 occupancy classifications.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
Assigned to occupancies that present a detonation hazard
Assigned to buildings that store explosives, blasting agents, or other hazardous materials
Represent the highest level hazard of all physical hazardous materials

## Slide 16: Understand Group H-2/High Hazard Level 2 occupancy classifications.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
Store materials that present a deflagration hazard
Include storage of flammable gases, pressurized flammable or combustible liquids, pyrophorics, higher-reactivity oxidizers, organic peroxides
Present a risk from accelerated burning of the material

## Slide 17: Understand Group H-3/High Hazard Level 3 occupancy classifications.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
Store or use hazardous materials that readily support combustion or present other physical hazards
Includes unpressurized flammable and combustible liquids, lower reactivity oxidizers and organic peroxides, flammable solids, oxidizing gases

## Slide 18: Understand Group H-4/High Hazard Level 4 occupancy classifications.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
Designed for storage of health hazard materials; for corrosives, and toxic and highly toxic materials exceeding the MAQ

## Slide 19: NOTE
The IBC and NFPA® 400 require a dual hazardous occupancy classification in buildings where the MAQ for physical and health hazard materials are exceeded.

## Slide 20: An explosion can result in either a detonation or deflagration.
Detonation
Principal heating mechanism is one of shock compression
Deflagration
Heat producing reaction characterized by a shock wave in the material
Heat-producing reaction occurs when a flammable gas, vapor or combustible dust is rapidly oxidized
Reaction zone progresses through the unburned material at a rate less than the speed of sound
Reaction zone progresses through the material at a rate greater than the speed of sound

## Slide 21: Some industries designate explosive materials as either primary or secondary explosives.
Primary explosives
Commonly used in detonators, which are devices used for initiating a detonation
Secondary explosives
Normally will not detonate when heated or ignited
Very sensitive materials that can be easily detonated and produce a fast pressure wave
Detonate when initiated by a shock wave created by a detonator
Courtesy of Scott Stookey, International Code Council, Washington D.C.

## Slide 22: Some industries designate explosive materials as either primary or secondary explosives.
(Cont.)

## Slide 23: Some industries designate explosive materials as either primary or secondary explosives.

## Slide 24: Hazardous occupancies have requirements common to the four occupancy classes.
Group H-1/High Hazard Level 1 occupancies
Continuous mechanical ventilation
Not permitted in mixed occupancy buildings
Require separate, stand-alone building without a basement
Require automatic sprinkler system complying with NFPA® 13
Must comply with sprinkler requirements in the particular NFPA® hazardous material standard
Sprinklers
Removes vapors or gases released
Fire-resistive separation
When a Hazardous/High Hazard occupancy is located in a mixed occupancy building
(Cont.)

## Slide 25: Hazardous occupancies have requirements common to the four occupancy classes.
IBC
Means of egress
Panic hardware
Common path of egress travel distances
Additional seismic safety features and special inspections are required for Group H occupancies based on the physical or health hazard classification of the stored materials
Group H/High-Hazard Level occupancies are more restrictive when compared to the other occupancies
Required in hazardous occupancies regardless of occupant load
Reduced
Exit access travel distances cannot be increased by installing an automatic sprinkler system

## Slide 26: REVIEW QUESTION
Describe the classification categories for hazardous and high-hazard occupancies.

## Slide 27: Codes prescribe specific administrative and engineering controls in Group H/High-Hazard occupancies.
Secondary containment
Mechanical ventilation systems
Automatic sprinkler protection

## Slide 28: Hazardous occupancies storing liquid or solids require spill control or secondary containment.
Hazardous occupancies storing liquid or solids
Secondary containment is prescribed when the outdoor MAQ is exceeded and iin all cases of exterior flammable and combustible liquid storage
Not required for compressed or liquefied compressed gases
Required to contain an accidental spill and keep it within the occupancy

## Slide 29: Using the floor surface of the hazardous occupancy will satisfy the requirements for spill control.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
Permissible if the container volume is less than 55 gallons (220 L) of liquids or 550 pounds (275 kg) of solids
IFC and NFPA® 400 require that the floor be liquid tight by using concrete or asphalt construction
Containment pallets can also satisfy the requirement for spill control

## Slide 30: Model fire codes require secondary containment for liquids and solids.
Liquids
When container volume is greater than 55 gallons (220 L) or the aggregate volume is greater than 1,000 gallons (4 000 L)
Solids
When individual container weight is greater than 550 pounds (275 kg) or the aggregate weight of hazardous materials is more than 10,000 pounds (5 000 kg)

## Slide 31: Model fire codes offer several compliance options for secondary containment.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
In all cases the design must provide a liquid-tight method of containing the spill from the largest container
Portable tank or stationary AST
Designs may utilize raised curbs or foundations constructed with a depression with sufficient depth to contain the contents
(Cont.)

## Slide 32: Model fire codes offer several compliance options for secondary containment.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
Another compliance option is a drainage system that captures a spill and drains it to an outdoor containment basin or a storage tank
Must not allow mixing of incompatible hazardous materials

## Slide 33: Model fire codes require monitoring of a secondary containment or drainage system.
Visual surveys
Electronic monitoring

## Slide 34: Know collection requirements for indoor secondary drainage systems.
Designed to collect the volume of the largest container or tank plus the discharge from an operating automatic sprinkler system
Model fire codes require that the system be capable of containing a minimum of 20 minutes of sprinkler water flow over the design area of the automatic sprinkler system or the area of hazardous occupancy, whichever is smaller

## Slide 35: Know collection requirements for outdoor secondary containment systems.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
With the exception of flammable and combustible liquids, model fire codes require secondary containment of hazardous materials outdoor storage when the outdoor MAQ is exceeded
Design for hazardous materials must contain the volume of the largest container or storage tank and contain the volume of rainfall produced in a 24-hour/25 year storm

## Slide 36: REVIEW QUESTION
What is the purpose of spill control and secondary containment?

## Slide 37: Know why Group H/High Hazard occupancies must have mechanical ventilation systems.
Systems provide adequate air movement to exhaust
Fumes
Vapors
Gases created by a container
Piping
Valve or component leak
Mechanical ventilation is not required for flammable solids

## Slide 38: Become familiar with the design requirements for mechanical exhaust systems.
Designed and constructed in accordance with the IMC or NFPA® 91
Must provide enough air at a sufficient velocity to capture gases or vapors
Design issue is the vapor density of the stored materials
Materials with vapor density greater than one require ventilation openings within 12 inches (300 mm) of the floor
Lighter-than-air vapors or gases require ventilation openings within 12 inches (300 mm) of the highest point of the room
(Cont.)

## Slide 39: Become familiar with the design requirements for mechanical exhaust systems.
Mechanical ventilation systems in hazardous occupancies are designed to provide a minimum air flow rate of one cubic foot per minute per square foot (cubic meter per minute per square meter) over the area of occupancy or space
Courtesy of Scott Stookey, International Code Council, Washington D.C.

## Slide 40: The selection of the duct and fan air foils (blades) is another consideration for inspectors.
Nonmetallic ducts may be required for corrosive materials
Materials like glass-fiber reinforced plastic or chlorinated PVC are acceptable but must be constructed of materials with limited flame spread and smoke production characteristics
Duct materials may be required to be listed for specific applications
In most cases the duct and air foils are of noncombustible construction

## Slide 41: Know how to determine the adequacy of emergency vents in stationary tanks.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
UL 142
Verify size
NFPA® 30
When flow rate on the vent equals or exceeds the rate on the nameplate, it complies
When flow rate on the vent is less than the value on nameplate, it does not
Requires nameplate on all shop-fabricated ASTs to indicate required emergency vent flow
Compare rate posted on the nameplate to the flow rate on the emergency vent
Requires all emergency vents to be permanently marked with their design flow rate

## Slide 42: REVIEW QUESTION
List some of the requirements for mechanical ventilation systems.

## Slide 43: Group H/High-Hazard occupancies require automatic sprinkler protection.
May be required throughout the building or only within the hazardous occupancy
Model fire codes generally do not dictate the type of sprinkler system, only that it must comply with NFPA® 13 requirements
NFPA® 13 requires specialized automatic sprinkler designs be installed for certain classes of physical hazard materials
Flammable and combustible liquids
Compressed gases that are classified as pyrophoric, flammable or oxidizers
Solid and liquid oxidizers and organic peroxides
(Cont.)

## Slide 44: Group H/High-Hazard occupancies require automatic sprinkler protection.
Courtesy of Scott Stookey, International Code Council, Washington D.C.
Of all the physical hazards, flammable and combustible liquids present the most variables in the design of an automatic sprinkler system
One method of satisfying the NFPA® 30 sprinkler design requirements is installing in-rack sprinklers with a horizontal barrier

## Slide 45: REVIEW QUESTION
List some of the requirements for automatic sprinkler systems in hazardous occupancies.

## Slide 46: Summary
During the course of an inspection, an inspector may encounter materials that may individually or in combination pose a risk or hazard.
(Cont.)

## Slide 47: Summary
It is essential for an inspector to recognize these potential hazards and have them removed, modify the way hazardous materials are stored, or provide for measures that reduce risks to acceptable levels.
(Cont.)

## Slide 48: Summary
The inspector must also be familiar with the maximum allowable quantities of hazardous materials that are permitted based on occupancy type and the materials themselves.
(Cont.)

## Slide 49: Summary
Hazardous and High-hazard occupancies require special attention because of the materials involved and potential for a catastrophic event.