## Slide 1
Fire Inspection and Code Enforcement
8th Edition Inspector II
Chapter 7 — Means of Egress

## Slide 2: Learning Objective 1
Explain the way to calculate occupant loads for multiuse occupancies.

## Slide 3: Know how to calculate the occupancy load for multiuse occupancies and multiple occupancies in one structure.
Multiuse occupancy
Multiple occupancies in one building
Nuilding or a portion of a building that contains two or more distinct occupancies
Building or a portion of a building that has more than one use
Occupant load is determined by the use that allows for the largest number of persons to occupy the building
Occupant load is determined by calculating the occupant load for each of the occupancies separately and then adding them
See Example 3 at the end of the chapter
See Example 4 at the end of the chapter

## Slide 4: REVIEW QUESTION
How is the occupancy load calculated for multiple occupancies in one building?

## Slide 5: Learning Objective 2
Explain the steps in determining means of egress.

## Slide 6: Determine the number of exits a room or building must have to enable people to leave quickly and safely.
Step 1: Determine the number of people who can move along the means of egress; capacity
Step 3: Evaluate the effectiveness
Step 2: Determine the arrangement of the exits

## Slide 7: Means of egress capacity must be at least equal to the occupant load.
Determined by floor area and based upon occupancy type
If a building or room has a means of egress capacity that is lower than the floor area occupant load, additional exits must be constructed
A room or building must have enough exits, located remotely from each other, and wide enough for people to safely exit

## Slide 8: An inspector needs to be able to determine the required width of the means of egress.
How
Must apply a numerical factor, expressed in terms of inches (millimeters) per person
Most common
0.3 inches (7.62 mm) per person for stairways
0.2 inches (5.08 mm) per person for ramps or level exit components, such as doors and corridors
(Cont.)

## Slide 9: An inspector needs to be able to determine the required width of the means of egress.

## Slide 10: Know the other factors for selected occupancies contained in model codes.
Buildings that are considered hazardous occupancies use 0.7 inches (17.78 mm) per person for stairways and 0.4 inches (10.16 mm) per person for ramps or level exit components
Each model code makes allowances based on whether the occupancy has an automatic sprinkler system

## Slide 11: Inspectors need to know how to determine exit capacity.
Calculate the capacity for each element
Exit access
Exit
Exit Discharge
Measure
Each element unobstructed at the width at the narrowest point
Determinant
Element with the smallest capacity decides total capacity of the means of egress
See Example 5 at the end of the manual chapter

## Slide 12: Inspectors need to know how to determine total exit capacity.
Determine the capacity of each exit
Add the results together
Procedures
Differ depending on whether the exit is at grade level
See Examples 6 and 7 at the end of the manual chapter
(Cont.)

## Slide 13: Inspectors need to know how to determine total exit capacity.
Stairways must be able to accommodate the greatest number of people expected to occupy any single floor above
ICC® model codes
Total of the exit capacities cannot be less than the sum of all the capacities
Means of egress cannot become narrower in the direction of travel or beyond any point where two or more exits converge

## Slide 14: Inspectors must be familiar with the requirements for the minimum number of exits.
Model code information
500 persons or less
Minimum number of exits
Special requirements and exceptions
At least two exits
Any balcony, mezzanine, story, or portion thereof
500 persons or greater
Minimum of three separate exits
Four or more exits required for 1,000 or more people
(Cont.)

## Slide 15: Inspectors must be familiar with the requirements for the minimum number of exits.
Ultimately, enforcement through citation may become the only remedy
In situations where the occupant load is consistently exceeded, inspectors should explore all possible alternatives for correction

## Slide 16: Multiple means of egress enable occupants to quickly locate an exit and leave during an emergency.
Be able to determine the location of multiple exits for new construction buildings
If insufficient, be able to recommend alternatives
Each model code specifies certain situations where a single exit is permitted
Decide if the maximum travel distance to existing exits is acceptable
Codes specify that exits should be as remote from each other as possible

## Slide 17: Inspectors need to understand the one-half diagonal rule.
When two exits are required, they should be located no less than half the length of the overall diagonal dimension of the room or building area
Diagonal is measured as a straight line from the nearest edges of the exit or exit access doors to each other
(Cont.)

## Slide 18: Inspectors need to understand the one-half diagonal rule.
When more than 2 exits are required
At least two doors will meet the minimum separation requirements
Other exits should be located in a manner so that they will be available if the primary exits become blocked or unavailable

## Slide 19: Be aware of the concerns surrounding location of exits.
Verify that designed exit plans follow all of the code-required factors for fire and life safety; even if changes have been made
Common to find modifications to assembly occupancies
Regardless of configuration, each room, space, or building must have adequate and appropriate exiting capabilities
Blocking an exit door in one location and building a new one in another location may not meet codes

## Slide 20: Model codes establish the maximum allowable travel distance to the nearest exit.
Refers to the total length of travel necessary to reach an exit
Maximum travel distances vary in model codes
Ends at the center of the exit doorway or other point at which the exit begins
Impacted by type of occupancy and automatic sprinkler systems

## Slide 21: Inspectors need to be aware of dead-end corridors.
Condition that exists when a corridor has no outlet to a means of egress and is more than 20 feet (6 m) in length

## Slide 22: Inspectors need to understand the common path of travel.
Path that all occupants must travel in one direction before choosing between two distinct paths to two separate exits
This distance is used in the calculation of total travel distance to an exit for the purpose of locating exits for a building or area
(Cont.)

## Slide 23: Inspectors need to understand the common path of travel.
(Cont.)

## Slide 24: Inspectors need to understand the common path of travel.

## Slide 25: Know what to ask about means of egress effectiveness.
What is the occupancy classification for the structure or portion of the structure?
Do the various parts of the means of egress comply with those allowed for the occupancy classification?
What is the total exit capacity in inches (mm), people, or both?
(Cont.)

## Slide 26: Know what to ask about means of egress effectiveness.
Does the travel distance to the nearest exit fall within the maximum distances for the occupancy classification?
Are there dead-end corridors or common paths of travel that must be considered?
Are all of the exits easily identifiable and accessible to different occupancy groups?
(Cont.)

## Slide 27: Know what to ask about means of egress effectiveness.
Are the means of egress properly illuminated and marked?
Do exit doors open easily? Are they equipped with panic hardware where required?
Are the parts of the means of egress free of obstructions?
What is the maximum number of occupants allowed for the particular occupancy or structure?
(Cont.)

## Slide 28: Know what to ask about means of egress effectiveness.
Are all interior finishes within the adopted code specified as to flame spread and smoke development limits for the occupancy?
Is the existing means of egress adequate for the occupancy classification or are additional exits needed?
When a building’s occupancy classification changes or alterations are made, are alterations to the means of egress requirements necessary?

## Slide 29: Use a consistent and logical approach to determining the means of egress requirements.
Step 1: Determine occupant load
Step 2: Determine clear width of each component
Step 3: Determine egress capacity of each component
Step 4: Determine most restrictive component of each route
Step 5: Determine if egress capacity is sufficient

## Slide 30: REVIEW QUESTION
Explain the steps used to determine the means of egress requirements for new and existing structures.

## Slide 31: Summary
Analysis of fires dating back over a century has shown that inadequate or blocked exits have been a significant factor in the loss of lives.
These tragic events have resulted in model code requirements for means of egress for all types of occupancy classifications.
(Cont.)

## Slide 32: Summary
The means of egress routes must conform to the requirements of the locally adopted building and fire code.
Equally important, emergency responders must be able to gain access to the structure.
(Cont.)

## Slide 33: Summary
An inspector is responsible for verifying that building occupants have an unimpeded ability to evacuate a structure or move to an area of refuge within the structure.
This ability is especially important for persons who are mobility impaired or who are not otherwise capable of seeking safety on their own.