## Slide 1
Fire Inspection and Code Enforcement
8th Edition Inspector I
Chapter 11 — Water Supply Distribution Systems

## Slide 2: Learning Objectives 1 & 2
Identify components of public water supply systems.
Identify characteristics of private water supply systems.

## Slide 3: Inspectors need to be familiar with types of water supply systems.
Public systems
Usually a function of local government
Local water department is usually a separate city utility
An elected board generally governs a state-authorized water district
(Cont.)

## Slide 4: Inspectors need to be familiar with types of water supply systems.
Private systems
Provide water under contract
Facility owners/occupants are responsible for inspection, testing, and maintenance
May be required to determine that private water supply distribution systems have been properly tested, inspected, and maintained
Must be familiar with basic principles of any private water supply distribution systems in the jurisdiction
May be specific to industrial facility or supply water to a residential subdivision
May encounter private water supply systems when performing site inspections or plans review for new construction

## Slide 5: REVIEW QUESTION
What is the difference between public and private water supplies?

## Slide 6: Know the basic components of public and private water supply systems.
Water supply source(s)
Processing/treatment facilities
Means of moving water
Water distribution/storage
Lakes, reservoirs, ponds, rivers, streams, aquifers, wells, or springs
Purification or desalination plants
Water pumps
Storage tanks, control valves, piping systems, and hydrants

## Slide 7: NOTE
A reservoir can serve as a water source and as part of the distribution system.

## Slide 8: Inspectors must be familiar with the design and reliability of private water supply distribution systems.
Well-maintained systems may provide a reliable source of water for fire protection
Small capacity or poorly maintained private water supply distribution systems should not be relied upon to provide all the water necessary
Reviewing documentation is the best method for evaluating the capabilities of the system

## Slide 9: REVIEW QUESTION
What are the common components of water supply systems?

## Slide 10: Inspectors must understand the basics of water supply sources.
Originates at the source
Distribution system for use
Moves to treatment or processing facility
Water
(Cont.)

## Slide 11: Inspectors must understand the basics of water supply sources.
Point of use
Individual residence
Commercial property
Water sources
Reservoirs (impounded water)
Suction tanks
Private water supply
Public fire hydrant
Pressure tanks
Gravity tanks
May be independent of public systems
(Cont.)

## Slide 12: Inspectors must understand the basics of water supply sources.
Before it can be used, most water must be processed to remove impurities
Most that depend on ocean water operate desalination plants and treatment plants
Once water has been used in most municipalities, it enters sanitary sewer systems
Most water purveyors operate water treatment plants
(Cont.)

## Slide 13: Inspectors must understand the basics of water supply sources.
Private water supply distribution systems
Commonly receive water from a municipal water supply distribution system
Separated from the private system by a water meter and check valve or an on-site water supply
May have its own water supply source independent of the municipal water distribution system

## Slide 14: A reservoir may be an open lake or pond or an enclosed structure.
Water may originate from the lake, pond, or well and be pumped into the reservoir

## Slide 15: Inspectors need to be familiar with suction tanks and pressure tanks.
Suction tanks
Located at ground level
Sized based on demand and system needs
Pressure tanks
Can be used for limited private fire protection services
Contain water under air pressure that is released when the system requires it
Should be provided with low/high water-level and air-pressure supervision gauges or devices
Provide water supply source for fire pumps

## Slide 16: Inspectors need to be familiar with gravity tanks.
Used to stabilize or balance pressures on distribution systems at times of peak demand
Tanks are elevated above the point of demand as a tower, on top of a structure, or on high terrain
When demand increases, water stored will begin to supplement water pumped
During low consumption, the pumps will fill tanks with excess water
Elevated tanks become an important fire protection feature during peak demand periods
Can require considerable maintenance and often require protection against freezing
Courtesy of Sand Springs (OK) Fire Department

## Slide 17: Understand the disadvantages of elevated tanks for fire protection water supplies.
Limitation of pressure available from the tank
A tank has to be 100 feet (30 m) high to generate a pressure of only 43 psi (301 kPa)
This pressure is not adequate to meet many modern fire protection system designs

## Slide 18: REVIEW QUESTION
Name the types of water sources.

## Slide 19: Be familiar with methods of moving water through water systems.
Gravity
Direct pumping
Combination system using both direct pumping and gravity

## Slide 20: A gravity system delivers water from the source to the distribution system without pumping equipment.
Difference in height of the water source and the point of use creates elevation pressure
Elevation pressure forces water throughout the water distribution system
Also known as elevation head pressure

## Slide 21: Inspectors need to be familiar with direct pumping systems.
Used when elevation pressure cannot provide sufficient pressure to meet needs of the community
One or more pumps installed in the distribution system create the pressure within the distribution system

## Slide 22: Inspectors need to be familiar with combination pumping systems.
Most communities use combination systems
Consist of both gravity tanks and the direct pumping process
Water is pumped into the distribution system
Elevated storage tanks provide gravitational pressure

## Slide 23: REVIEW QUESTION
What methods are used to move water?

## Slide 24: Inspectors need to be familiar with water distribution systems.
Consists of a network of pipes, storage tanks, control valves, and hydrants throughout the community or service area that carry the water under pressure to the points of use

## Slide 25: Inspectors need to know the role of piping in water distribution systems.
Fire hydrants, gate valves, elevated storage, and reservoirs are secondary parts of the distribution system
The term “grid” or “gridiron” describes the interlocking network of water mains that compose a water distribution system

## Slide 26: A water distribution system consists of different types of water mains.
Primary feeders
Distributors
Convey large quantities of water to various points and supply smaller secondary feeder mains
Fire hydrants are rarely attached directly
Large pipes or arterial mains, with relatively widespread spacing
Intermediate pipes that interconnect with primary feeder lines to create a grid
May form an intermediate grid between secondary feeders
May be dead-end lines
Small
Secondary feeders
Control valves can isolate each secondary feeder
Serve individual fire hydrants and commercial and residential consumers

## Slide 27: Know the characteristics of water distribution systems.
Generally designed using hydraulic calculation software intended to provide constant pressure range and reliable delivery throughout the system
Grid or loop system is designed to provide constant pressure or flow when pipes or the grid need repair
High demand in one area does not reduce water flow in other areas
Dead-end lines can result in reduced water flows

## Slide 28: Know the importance of connections in water distribution systems.
Connected to the piping system
May be through fire hydrants that are used for fire protection
Provide access to the water supply system
May be through water flow control valves and flowmeters at the point where customers gain water from the system

## Slide 29: Private fire protection system components are maintained by the property owner.
Located on private property
Trained facility employees or individuals certified to perform construction and repairs are responsible for exercising the system control valves annually
Generally, components are similar to the ones found on public water supply distribution systems

## Slide 30: Some distribution systems maintain separate piping for fire protection and domestic or industrial services.
Characteristics
Separate distribution systems are cost-prohibitive for most municipal applications
Advantages
Property owner has control over the water supply source
Neither system (fire protection or domestic/industrial services) is affected by service interruptions to the other system
Economically practical in many private applications
This separation differs from most municipal water supply distribution systems in which fire hydrants are connected to the same mains that supply water for domestic or industrial use

## Slide 31: Know the role of storage tanks in water distribution systems.
May be located throughout the system
Usually constructed of steel or concrete

## Slide 32: Know the role of control valves in water distribution systems.
Installed throughout the water distribution system
Generally located on the small line at the point where it attaches to the large line
Used to isolate the flow of water
Sections of distribution lines, secondary feeders, and primary feeders
The entire system
Individual hydrants or properties
(Cont.)

## Slide 33: Know the role of control valves in water distribution systems.
Spaced so that a minimum length of the water distribution system will be out of service if it is necessary to close a valve
Workers close valves to initiate repairs to the system or to isolate a water main break
Should be exercised at least once a year

## Slide 34: Know the types of control valves in water distribution systems.
Indicating
Shows whether the valve is open, closed, partially closed
Usually used in private systems
Nonindicating
No visual indicator for open or closed valve
Usually located underground
PIV and OS&Y

## Slide 35: Know how to access buried valves with valve keys.
Covers located in or near the street indicate access to control valves
If a buried valve is properly installed, the valve is operated through a valve box with a special valve key
Water purveyors commonly keep the valve key, although it could also be carried on fire apparatus

## Slide 36: Control valves may be gate valves or butterfly valves.
Gate valves
Usually the non-rising stem type
Butterfly valves
Usually have a rubber or rubber-composition seat that is bonded to the valve body
As the operator turns the valve nut, the gate rises or lowers to control the water flow
Valve disk rotates 90 degrees to open or close the valve

## Slide 37: Water supply lines may also have a water flowmeter and a backflow preventer.
Flowmeter
Determines the quantity of water that the facility uses for billing purposes
Backflow preventer
Prohibits potentially contaminated water from flowing into the public water system

## Slide 38: Two sources of water may serve some private facilities for fire protection.
Municipal systems
Private source
May provide nonpotable (not for drinking) water
Officials need to take adequate measures to prevent contamination caused by backflow into the municipal water system
Some jurisdictions do not allow interconnection of potable and nonpotable water supply systems; means the property is required to maintain two separate distribution systems

## Slide 39: Learn the characteristics of dry-barrel fire hydrants.
Used in climates that have freezing temperatures
Control valve is on the distribution line below the frost line
Stem nut used to open and close the control valve is located on top
Any water remaining in a closed dry-barrel hydrant drains through a small drain valve that opens at the bottom
Water flows into the hydrant only when a firefighter operates the stem nut
Use a hydrant wrench to turn the stem to opens/closes the valve

## Slide 40: Learn the characteristics of wet-barrel fire hydrants.
Used in mild climates
Compression valves are usually at each outlet
Features the valve at the hose outlet
Water remains in the hydrant at all times
May be another control valve in the top of the hydrant to control the water flow to all outlets

## Slide 41: There are two components on standard hydrant discharge outlets.
At least one large (4- or 4½-inch [100 mm or 115 mm]) outlet, often referred to as the steamer connection or pumper outlet connection
Two hose outlet nozzles for 2½-inch (65 mm) couplings

## Slide 42: Know the inspection requirements for fire hydrants.
Should occur at least once a year
In some jurisdictions, fire companies perform these inspections
Records of hydrant inspections and maintenance performed should be maintained
Inspectors need accurate reports of observations and tests to evaluate operational readiness
Hydrants may be painted to designate ownership and flow capacity

## Slide 43: Know classifications and markings of municipal fire hydrants.

## Slide 44: Know the inspection requirements for private fire hydrants.
Fire departments depend on hydrants working during a fire incident
Periodic inspections, maintenance, and flow testing must be performed
Inspectors should note signs of damage or disrepair and report them
Qualified individuals must inspect private hydrants and provide documentation for review, according to NFPA® 25 and ISO guidelines

## Slide 45: REVIEW QUESTION
List types of water distribution systems.

## Slide 46: Learning Objective 3
Explain water supply testing.

## Slide 47: Inspectors may be assigned the task of analyzing the water supply for the municipality or service area.
May perform analysis periodically, when the water distribution system is altered or expanded, or when applications are made for new construction
May be required to witness testing of private water supply distribution systems; review fire protection system documents based on these tests
Analysis may involve flow testing hydrants; reviewing data provided

## Slide 48: Inspectors need to know what fire flow tests include.
Measurement of static pressure and residual pressure
Formulas and calculations used to determine available water from these tests

## Slide 49: Understand additional characteristics of fire flow tests.
Determine rate of fire flow available for fire suppression at various locations within the distribution system
Hydrant pressure varies between periods of peak demand and minimal demand

## Slide 50: Know what calculations or graphical analyses from fire flow tests provide.
Amount of water flow from individual hydrants
Water flow pressures
Quantity of water available at any pressure
Pressure available across a wide range of flows

## Slide 51: Understand why fire flow tests are important.
Essential when fire companies prepare preincident plans
May also indicate weak points in a water distribution system
Plan improvements in an existing system
Design extensions to newly developed areas

## Slide 52: Understand what fire flow tests repeated at the same locations semiannually reveal.
Loss in carrying capacity of water mains
Closed or partially closed valves
Need for improving certain arterial mains

## Slide 53: Understand when fire flow tests should be conducted.
After extensive water main improvements
Following construction of water line extensions
On a regular predetermined basis on existing portions of the distribution system

## Slide 54: REVIEW QUESTION
What can an inspector learn from testing water supplies?

## Slide 55: Learning Objective 4
Explain fire hydrant inspections.

## Slide 56: Know what an inspector must do to perform fire flow tests and analyze the results.
Operate a pitot tube and gauge
Calculate how much water is flowing from a hydrant
Determine residual pressure required for the water distribution system when water is flowing from the system
Perform the test, adhere to test precautions, determine possible obstructions in the system, and analyze results based on computations

## Slide 57: Understand inspection needs for fire hydrants.
Should be performed on an annual basis
Should be inspected before fire flow tests begin
Inspectors or emergency response companies may perform inspections as part of their normal duties
May be performed as part of the fire flow tests

## Slide 58: Know the materials needed to complete fire hydrant inspections.
Notebook
Gauging device
Approved lubricant
Small, flat brush
Gate valve key
Pressure gauge and a tapped hydrant cap
Appropriate pitot tube and gauge
Hydrant wrench
Water stream

## Slide 59: Know what to look for during fire hydrant inspections.
Check for obstructions near the hydrant such as sign posts, utility poles, shrubbery, or fences
Check outlet(s) to verify that they face the proper direction; that there is clearance between the outlet and surrounding ground
Check for mechanical damage
Check the condition of the paint for rust or corrosion
(Cont.)

## Slide 60: Know what to look for during fire hydrant inspections.
Check water flow by having the hydrant fully opened
Check that a dry-barrel hydrant drains once the stem valve is closed
Verify that discharge outlet caps are not painted shut

## Slide 61: REVIEW QUESTION
List the tools needed to perform a fire hydrant inspection.

## Slide 62: Learning Objective 5
Describe how to use a pitot tube and gauge to take flow readings.

## Slide 63: An inspector must be familiar with the use of a pitot tube and gauge for determining hydrant flow rates.
Step 1
Open the petcock (small faucet or valve used to control the flow of liquids) on the pitot tube and verify that the air chamber is drained
Close the petcock
(Cont.)

## Slide 64: An inspector must be familiar with the use of a pitot tube and gauge for determining hydrant flow rates.
Step 2
Blade should be parallel to the outlet opening with the air chamber kept above the horizontal plane passing through the center of the stream
This position increases efficiency of the air chamber and helps avoid needle fluctuations
Edge the blade into the stream with the small opening or point centered in the stream and held away from the hydrant butt or nozzle approximately one-half the diameter of the opening
Step 3
Check the velocity pressure reading from the gauge; if the needle is fluctuating, read and record the value located in the center between the high and low extremes
(Cont.)

## Slide 65: An inspector must be familiar with the use of a pitot tube and gauge for determining hydrant flow rates.
Step 4
After the test is completed, open the petcock and be certain that all water drains from the assembly before storing it

## Slide 66: Understand the proper way to hold a pitot tube and gauge for determining hydrant flow rates.
Note that the operator in the figure grasps the pitot tube just behind the blade with the first two fingers and thumb of the left hand, while the right hand holds the air chamber
The little finger of the left hand rests upon the hydrant outlet or nozzle tip to steady the instrument
Unless some effort is made to steady the pitot tube, the movement of the water will make it difficult to get an accurate reading

## Slide 67: Understand another way to hold a pitot tube and gauge for determining hydrant flow rates.
In the figure the left-hand fingers are split around the gauge outlet; the left side of the fist is placed on the edge of the hydrant orifice or outlet
The blade can then be sliced into the stream in a counterclockwise direction
The right hand steadies the air chamber

## Slide 68: REVIEW QUESTION
List the steps in the procedure for using a pitot tube and gauge.

## Slide 69: Learning Objective 6
Explain how to use flow test computations.

## Slide 70: Understand where to find tables for nozzle/outlet discharge.
Prepared tables
Tables developed by the jurisdiction

## Slide 71: Inspectors need to be familiar with the flow formulas.
(Cont.)

## Slide 72: Inspectors need to be familiar with the flow formulas.
The constant 29.83 (0.0667766) is derived from the physical laws relating water velocity, pressure, and conversion factors
Formula was derived by assigning a coefficient of 1.0 for an ideal frictionless discharge orifice
Actual hydrant orifice or nozzle will have a lower coefficient of discharge, reflecting friction factors that slow the flow velocity
Coefficient will vary with type of hydrant outlet or nozzle used
Conveniently leave the answer in gallons per minute (L/min)

## Slide 73: When using a hydrant orifice, feel the inside to determine which type of hydrant outlet is being used.
Refer to manufacturer's recommendations for determining the coefficient of discharge for a specific nozzle

## Slide 74: Understand how to perform flow test computations.
Flow formulas depend on the actual internal diameter of the outlet or nozzle opening being used
Ruler with a scale that measures to at least 1/16th of an inch (1.5 mm) should be used to measure the diameter of the outlet or nozzle opening
Generally, 2½-inch (65 mm) outlets should be used to conduct hydrant flow tests because the stream from a large hydrant outlet (4 to 4 ½ inches [100 mm to 115 mm]) contains voids; the entire stream of water is not solid

## Slide 75: Understand how to perform flow test computations on large outlets.
The listed formulas alone will not give accurate results for flows using large outlets
If it is necessary to use the large outlets, use a correction factor to give more accurate results
(Cont.)

## Slide 76: Understand how to perform flow test computations on large outlets.
Formulas allow the computation of total flow from the flowing hydrants when performing an area fire-flow test
Formulas indicate the flow from the hydrant only at the time of the test
High-risk areas or locations with large, daily fluctuations in demand may necessitate multiple tests to determine the minimum flow available

## Slide 77: REVIEW QUESTION
List the physical laws from which the constant used in the flow test formula is derived.

## Slide 78: Know what the minimum required residual pressure is for computing available water.
20 psi (140 kPa)
Established by fire protection engineers

## Slide 79: Know how residual pressure is defined.
Enough pressure to overcome friction inside
Short 6-inch (150 mm) branch pipe
Hydrant
Apparatus intake hose

## Slide 80: Residual pressure must also allow a safety factor to compensate for gauge error.
The Environmental Protection Agency (EPA) and many state health departments require the 20 psi (140 kPa) minimum to prevent external ground (surface) water or other contaminants and pollutants from being drawn into the distribution system at pipe connection points

## Slide 81: Understand how pressure differentials impact water systems.
Can collapse a water main
Fire apparatus operating at a low system pressure may draw the entire capacity of the system at a location
If a discharge valve is turned off too quickly, a water hammer (sudden surge in pressure) will be generated; may be transferred to the water main, resulting in damaged or broken system components
Can create cavitation (implosion of air pockets drawn into fire pumps connected to the system)

## Slide 82: REVIEW QUESTION
Explain residual pressure.

## Slide 83: Inspectors need to know general information about fire flow test procedures.
Static pressure and residual pressure should be taken from a test hydrant as close as possible to the location requiring the test results
Flow hydrants are hydrants where pitot gauge readings are taken to find their individual flows
Readings are then added to find the total flow
(Cont.)

## Slide 84: Inspectors need to know general information about fire flow test procedures.
In general, the test hydrant should be located between the flow hydrant and the water supply source when flow testing a single hydrant
(Cont.)

## Slide 85: Inspectors need to know general information about fire flow test procedures.
Flow hydrant should be downstream from the test hydrant
Actual direction of flow in the system is difficult to determine
Consult water department personnel for assistance
When flow-testing multiple hydrants, the test hydrant should be centrally located relative to the flow hydrants

## Slide 86: NOTE
Water is actually never discharged from a test hydrant; rather, a pressure gauge cap is placed on the discharge and the hydrant is fully opened.

## Slide 87: Inspectors need to know fire flow test procedures.
Step 1
Step 2 (pictured)
Locate personnel at all hydrants to be used
Remove a hydrant cap from the test hydrant; attach the pressure gauge cap with the petcock in the open position
After checking the other caps for tightness, slowly open the hydrant by turning the operating nut several turns
Once air has escaped and a steady stream of water is flowing, close the petcock and fully open the hydrant
(Cont.)

## Slide 88: Inspectors need to know fire flow test procedures.
Step 3
Read and record the static pressure as seen on the pressure gauge
Step 4
Remove cap(s) from the outlet(s) on the flow hydrants
Check and record the hydrant coefficient and the actual inside diameter of the orifice when using a hydrant outlet
If a nozzle is placed on the outlet, check and record its coefficient and the diameter of the nozzle orifice
(Cont.)

## Slide 89: Inspectors need to know fire flow test procedures.
Step 5
Open flow hydrants as necessary and read and record the pitot gauge reading of the velocity pressures; the individual at the test hydrant simultaneously reads and records the residual pressure
(Cont.)

## Slide 90: NOTE
The residual pressure should not drop below 20 psi (140 kPa) during the test; if it does, the number of flow hydrants must be reduced.
(Cont.)

## Slide 91: Inspectors need to know fire flow test procedures.
Step 6
Step 7
Slowly close the flow hydrant to prevent water hammer
Report any hydrant defects
Check pressure gauge on the test hydrant for a return to normal operating pressure, then close the hydrant
Open petcock valve to prevent a vacuum on the pressure gauge
Remove pressure gauge cap
After checking for proper drainage, replace and secure hydrant cap
Report any hydrant defects
After checking for proper drainage, replace and secure all hydrant caps

## Slide 92: Know how to determine the number of hydrants to open.
General guidelines
Enough hydrants should be opened to drop the static pressure by at least 10 percent
Depends on an estimate of the flow available in the area
For more accurate results
Increase the pressure drop to 25 percent to 60 psi (420 kPa)
Graphical analysis or mathematical calculations can then determine the flow available at 20 psi (140 kPa)

## Slide 93: Know what to do when no flow pressure can be read on the pitot gauge.
Can occur when water mains have very low pressure
Flow orifice must be reduced by using a straight stream nozzle with tips smaller than 2½ inches (65 mm)
Nozzle is placed on the hydrant outlet to increase flow velocity to a point where velocity pressure is measurable
Using these nozzles will require adjustment in the water flow calculation that must include the smaller nozzle diameter and corrected coefficient of friction for the tip

## Slide 94: REVIEW QUESTION
Describe the procedure to conduct a flow test.

## Slide 95: Precautions taken help avoid injuries and minimize property damage.
Timing
Traffic control
Notify businesses in the area to reduce the number of false reports of possible water main breaks
Notifications promote a positive working relationships
Pedestrian and vehicular traffic during all phases of the testing may require assistance from local law enforcement personnel
Conduct flow tests in busy areas at nonpeak hours
Notifications
Before conducting a flow test, notify a water department official

## Slide 96: Know what safety measures to take during hydrant testing.
Wear protective items like a helmet, gloves, eye protection, reflective safety vests
Erect traffic safety signs on busy streets
Tighten caps on hydrant outlets that are not being used
Do not stand in front of closed caps
Do not lean over the top of a hydrant when operating it
Do not flow water during freezing weather

## Slide 97: It is also important to take steps to protect the surrounding property during a test.
Open and close hydrants slowly to avoid water hammer
Do not flow hydrants where drainage is inadequate
Check downstream to see where the water will flow
Take proper measures beforehand to slow or stop traffic
A good rule to follow is “When in doubt, do not flow!”
If there are difficulties, consider solutions so that the test can be completed without disruptions or property destruction

## Slide 98: WARNING
Do not leave deep standing water resulting from a hydrant test unattended in retention basins in locations where children are playing. Wait until the water has been absorbed or drained before leaving the area. Do not allow children to play in runoff water.

## Slide 99: REVIEW QUESTION
What precautions should an inspector take when conducting water flow tests?

## Slide 100: Reduced water flow may be a result of encrustations.
Definition
Location
Growths, crusts, tubercular lump corrosion, or rust on the inside walls of water mains
Around the inside wall of a water main
Eventually narrows the actual diameter of the pipe to a point where its capacity is greatly impaired
(Cont.)

## Slide 101: Reduced water flow may be a result of encrustations.
Causes
Chemicals in the water
Accumulation of various salts due to oxidation
Biological or organism growth
Biodegradation of water agents and pipe materials
Progressive growth of rust deposits of iron pipes
Biological reactions produced by organisms present in most water supplies

## Slide 102: Reduced water flow may be a result of sedimentation deposits.
Sedimentary decay (mud, clay, or leaves)
Foreign matter other than sediment (stones, tools, wood, or lead)
Dead organisms
Decayed vegetation found chiefly in the bottom of a water main
Especially common in large, low-velocity portions of a system; dead-end idle flow parts of a system

## Slide 103: Reduced water flow may be a result of malfunctioning components.
Valves
Pipes
Pumps
Closed or partially closed
Leaking or broken pipe section or mains
Worn or damaged impellers or pressure adjustments set too low for the demand of the system

## Slide 104: Reduced water flow may be a result of foreign matter and increased friction loss.
Foreign matter other than deposits
Chunks of lead (from ball and spigot joints)
Increased friction loss
Boards
Crowbars
Tool handles
Stones
Other materials
Combination of encrustation, sedimentation, partially closed or closed valves, and foreign matter will result in increased friction loss

## Slide 105: Inspectors should be aware of the consequences of stuck or partially closed valves.
Not noticed during normal water usage
High-friction loss would reduce the water volume available for fire suppression systems or fire suppression operations
Routine testing can locate partially closed valves before they pose a problem

## Slide 106: REVIEW QUESTION
What are some of the obstructions an inspector may encounter when conducting water flow tests?

## Slide 107: Graphical analysis is one way to compute fire flow test results.
Fire flow chart is a logarithmic scale developed to simplify the process
Can multiply or divide the figures on the vertical and/or horizontal scales by a constant if necessary to fit any situation
Chart is accurate to a reasonable degree if an inspector uses a fine-point pencil or pen when plotting results

## Slide 108: Know the procedure for conducting a graphical analysis.
Step 1
Step 2
Step 3
Step 4
Determine which gpm (L/min) scale to use
Locate and plot the static pressure on the vertical scale at 0 gpm (0 L/min)
Locate the total water flow measured during the test on the chart
Locate the residual pressure noted during the test on the chart
(Cont.)

## Slide 109: Know the procedure for conducting a graphical analysis.
Step 5
Step 6
Step 7
Plot the residual pressure above the total water flow measured
Draw a straight line from the static pressure point through the residual pressure point on the water flow scale
Read the gpm (L/min) available at 20 psi (140 kPa) and record the figure; this reading represents the total available water
(Cont.)

## Slide 110: NOTE
Inspectors must understand that pitot gauge pressures are never plotted on the graph; only the flow that corresponds to the pitot gauge pressures is used.

## Slide 111: Know the procedure for conducting a graphical analysis.
(Cont.)

## Slide 112: Know the procedure for conducting a graphical analysis.

## Slide 113: The mathematical method uses a variation of the Hazen-Williams formula.
Example 6 (US)
Mathematical Method for Determining Fire Flow

## Slide 114: Personnel more commonly complete these calculations with software.
Still important to understand the formulas
Data is entered from the flow test, and available water supply is automatically determined
Several programs available

## Slide 115: REVIEW QUESTION
List the steps involved in a graphical analysis.

## Slide 116: Summary
Adequate water supply systems are critical for agriculture, industrial, domestic and fire protection uses.
(Cont.)

## Slide 117: Summary
Because water-based fire suppression in the form of water application or sprinkler systems are often the first line of defense against a fire, inspectors must know that the water supply systems in their districts are adequate.
(Cont.)

## Slide 118: Summary
Water systems may be public or private, and the responsibility for seeing that the systems are inspected and maintained varies.
Nonetheless, inspectors need to be aware of water supply systems and methods for testing the adequacy of water supplies.