Skill Sheet 14-4

Objective 11	Operate sprinkler system control valves. [NFPA 1001, 4.3.14]

| ## Student Name: |  | ## Date: |  |
| --- | --- | --- | --- |

Directions

For this skill sheet, students will operate sprinkler system control valves. Students should complete both methods. This skill requires students to work as members of a team. Before the skill begins, indicate to students what position to take. Students should rotate positions to practice the skill as needed.

Always follow manufacturer’s recommendations and local standard operating procedures (SOPs) when performing all skills. Students must properly wear appropriate PPE when performing this skill.

Resources

| - Automatic sprinkler system valves (OS&Y and PIV) | - Appropriate PPE |
| --- | --- |

Criteria & Evaluation Comments

Criteria (determined by the AHJ)

After the student has completed the skill sheet, write comments below.

Evaluator/Student Comments

| Pass |  |  | Fail |  |
| --- | --- | --- | --- | --- |

| Evaluator Signature | Date |  | Student Signature | Date |
| --- | --- | --- | --- | --- |

Skill Sheet 14-4 
Assessment

Objective 11	Operate a sprinkler system control valve. [NFPA 1001, 4.3.14]

| Task Steps |  | Yes | No |
| --- | --- | --- | --- |
|  | OS&Y |  |  |
| 1. | Unlock and remove the chain, if necessary. |  |  |
| 2. | Turn the OS&Y valve clockwise until the valve is fully closed and the stem is flush with the wheel. |  |  |
| 3. | Open the OS&Y valve by turning it counterclockwise until fully opened. |  |  |
| 4. | Back off the OS&Y valve one-quarter turn clockwise. |  |  |

| Task Steps |  | Yes | No |
| --- | --- | --- | --- |
|  | PIV |  |  |
| 1. | Unlock the PIV wrench from the PIV body. |  |  |
| 2. | Position the PIV wrench on the stem nut. |  |  |
| 3. | Close the PIV valve, turning it clockwise slowly until the target window indicates CLOSED or SHUT. |  |  |
| 4. | Open the PIV valve, turning it counterclockwise until it is fully open and the target window indicates OPEN. |  |  |
| 5. | Back off the PIV valve, turning it clockwise one-quarter turn, ensuring that the target window remains OPEN. |  |  |
| 6. | Replace and lock the wrench onto the PIV body. |  |  |